JARVIS – FORMULAE & BUSINESS LOGIC (Module by module)

- Facility Datasheet

- Total influent BOD lbsday=

Influent flow-Diverted flow MGD x BOD mgLx 8.34

- Total MLVSS lbs= Total Vol of Aeration Basin million gal x MLSS mgLx 8.34 x (MLVSSMLSSratio)

- FM Ratio=Total BOD lbsdayTotal MLVSS (lbs)

- FMDO Ratio=FMDO (mgL)

- Solids Inventory, Aeration Basin AB (lbs)=Total Vol of Aeration Basin million gal x MLSS mgLx 8.34

- Solids Inventory, Secondary Clarifier SC (lbs)=MLSS mgL+RAS mgL2x Avg side water depth of Clarifier ft -Avg Sludge Blanket depth (ft)Avg side water depth of Clarifier (ft) x 
(Total Vol of Secondary Clarifiers million gal) x 8.34

- Solids leaving treatment lbsday=WAS flow GPM x Mins of operation per hr x 24 x 10-6 x RAS mgLx 8.34+Avg Effluent flow at Weirs MGD x ESS mgLx 8.34

- Yield coefficient=WAS flow GPM x Mins of operation per hr x 24 x 10-6 x RAS mgLx 8.34Influent flow-Diverted flow MGD x BODi mgL x 8.34 -{Avg Effluent flow at Weirs MGD x BODe mgLx 8.34}

- SRT days=Solids Inventory, AB (lbs)Solids leaving treatment (lbsday)

- MCRT=Solids inventory,  AB lbs + Solids inventory,  SC (lbs) Solids leaving treatment lbsday

- HLR galdaysq.ft=Influent flow-Diverted flow+RAS flow MGD x 106Total Surface Area of Aeration Basin (sq. ft)

- OLR lbsdaysq.ft=Total BOD (lbsday)Total Surface Area of Aeration Basin (sq. ft)

- HRT,AB hrs=Total Vol of Aeration Basin (million gal) x 24Influent flow-Diverted flow+RAS flow MGD

- SDT,AB hrs=Solids Inventory, Aeration Basin AB (lbs) x 24Influent flow-Diverted flow+RAS flow MGD x MLSS mgL x 8.34

- SOR galdaysq.ft=Influent flow-Diverted flow+RAS flow MGD x 106Total Surface Area of Secondary Clarifiers (sq. ft)

- WOR galdaylinear ft=Influent flow-Diverted flow+RAS flow MGD x 106Total length of weirs (linear ft)

- SLR lbsdaysq.ft=Influent flow-Diverted flow+RAS flow MGD x MLSS mgL x 8.34Total Surface Area of Secondary Clarifiers (sq. ft)

- HRT,SC hrs=Influent flow-Diverted flow MGD x 24Total Vol of Secondary Clarifiers (million gal)

- SDT,SC hrs=Solids Inventory, Secondary Clarifier SC lbs x 24RAS flow MGD x RAS mgL x 8.34

- Problem Index : N/A

- Training & Verification

- Source Identification

- Inspection

- Testing

- Troubleshooting

- Recommendations – N/A