S1_ RAS : Formulae

Summary Sheet: In this sheet, the user inputs value for SSV after deciding a standard settling time. Note, the field ‘Ideal settling time considered’ is not part of any formula.

Target RAS :

If able to get from Facility Datasheet

INPUTS:

- Total Flow entering Aeration Basins including RAS = Facility Datasheet - Inputs: 
Total Flow entering Aeration Basins (F(AB))

- Current RAS Flow = Facility Datasheet - Inputs: 
RAS Flow (F(RAS))

- Volume of Settleometer = User Input

- Ideal settling time considered (minutes) = User Input

- SSV = User Input

- T(WASs) = Facility Datasheet - Inputs: 
Minutes of operation of Secondary WAS pump per hour, on average (T(WASs))

OUTPUTS:

- Target F(RAS) in MGD as per above formula. Then use the following unit conversion table.

Unit Conversions:

| MGD to GPD | GPD to GPM |
| --- | --- |
| GPD = MGD . 10^6 | GPM = GPD / (24. 60) |

If unable to get from Facility Datasheet

INPUTS: User inputs for fields mentioned in RAS sheet.

OUTPUTS:

Target F(RAS) in MGD as per above formula. Then use the following unit conversion table.

Unit Conversions:

| MGD to GPD | GPD to GPM |
| --- | --- |
| GPD = MGD . 10^6 | GPM = GPD / (24. 60) |

Required Change in RAS Flow = Target RAS Flow - Current RASWAS Flow

The difference can be either (+) or (–). If (+) the operator has to increase RAS flow, If (–) the operator has to decrease RAS flow

The increase or decrease cannot be more than 12.5% per day. Therefore, day-by-day schedule of flow changes is prepared as follows:

| Day | Required Flow Change (+) or (-), Applies to all Qr(MGD), Qr(GPD), Qr(GPM) |
| --- | --- |
| Day 1 | = IF( <= 0.125 x Current RAS, print(), ELSE(print(0.125 x Current RAS)) |
| Day 2 | = IF( – Day1 <= 0.125 x (Current RAS + Day1), print( – Day1), ELSE(print(0.125 x (Current RAS + Day1)) |
| Day 3 | = IF( – Day1 – Day2 <= 0.125 x (Current RAS + Day1 + Day2), print( – Day1 – Day2),ELSE(print(0.125 x (Current RAS + Day1 + Day2)) |
| Day 4 | = IF( – Day1 – Day2 – Day 3 <= 0.125 x (Current RAS + Day1 + Day2 + Day3), print( – Day1 – Day2 – Day3), ELSE(print(0.125 x (Current RAS + Day1 + Day2 + Day3)) |
| Day 5 | = IF( – Day1 – Day2 – Day 3 – Day4 <= 0.125 x (Current RAS + Day1 + Day2 + Day3 + Day4), print( – Day1 – Day2 – Day3 – Day4), ELSE(print(0.125 x (Current RAS + Day1 + Day2 + Day3 + Day4)) |
| Day 6 | = IF( – Day1 – Day2 – Day 3 – Day4 – Day5 <= 0.125 x (Current RAS + Day1 + Day2 + Day3 + Day4 + Day5), print( – Day1 – Day2 – Day3 – Day4 – Day5), ELSE(print(0.125 x (Current RAS + Day1 + Day2 + Day3 + Day4 + Day5)) |
| Day 7 | = IF( – Day1 – Day2 – Day 3 – Day4 – Day5 – Day6 <= 0.125 x (Current RAS + Day1 + Day2 + Day3 + Day4 + Day5 + Day6), print( – Day1 – Day2 – Day3 – Day4 – Day5 – Day6), ELSE(print(0.125 x (Current RAS + Day1 + Day2 + Day3 + Day4 + Day5 + Day6)) |
| Day 8 | = IF( – Day1 – Day2 – Day 3 – Day4 – Day5 – Day6 – Day7 <= 0.125 x (Current RAS + Day1 + Day2 + Day3 + Day4 + Day5 + Day6 + Day7), print( – Day1 – Day2 – Day3 – Day4 – Day5 – Day6 – Day7), ELSE(print(0.125 x (Current RAS + Day1 + Day2 + Day3 + Day4 + Day5 + Day6 + Day7)) |
| Day 9 | = IF( – Day1 – Day2 – Day 3 – Day4 – Day5 – Day6 – Day7 – Day8 <= 0.125 x (Current RAS + Day1 + Day2 + Day3 + Day4 + Day5 + Day6 + Day7 + Day8), print( – Day1 – Day2 – Day3 – Day4 – Day5 – Day6 – Day7 – Day8), ELSE(print(0.125 x (Current RAS + Day1 + Day2 + Day3 + Day4 + Day5 + Day6 + Day7 + Day8)) |
| Day 10 | = IF( – Day1 – Day2 – Day 3 – Day4 – Day5 – Day6 – Day7 – Day8 – Day9 <= 0.125 x (Current RAS + Day1 + Day2 + Day3 + Day4 + Day5 + Day6 + Day7 + Day8 + Day9), print( – Day1 – Day2 – Day3 – Day4 – Day5 – Day6 – Day7 – Day8 – Day9), ELSE(print(0.125 x (Current RAS + Day1 + Day2 + Day3 + Day4 + Day5 + Day6 + Day7 + Day8 + Day9)) |

Extra 1 Sheet: In this sheet, the user has to decide the correct settling time from the graph. The graph is between SSC (y-axis) and Time (x axis). The user locates a “bend” in the graph and accordingly inputs the ideal x and y-values. The x-value ‘Time’ is not part of any formula.

- The user performs the experiment and records observations for SSV for the corresponding Time values.

- From SSV input, SSC is calculated using the formula below:

- Line graph is plotted between SSC (y-axis) and Time (x-axis)

- User has to look at graph, locate “bend” and enter the ideal SSC and Time.

- The Target RAS (MGD) is calculated from SSC value as follows:

Remaining formulae same as Summary sheet :

- Target Qr GPD=Qr MGD . 106

- Target Qr GPM=Qr GPD24 .  60

- Total required change in RAS flow ()= Target RAS-Current RAS
The difference can be either (+) or (–) , 
If (+) the operator has to increase RAS flow, If (–) the operator has to decrease RAS flow

- The increase or decrease cannot be more than 12.5% per day. Therefore, day-by-day schedule of flow changes is prepared as follows:

| Day | Required Flow Change (+) or (-), Applies to all Qr(MGD), Qr(GPD), Qr(GPM) |
| --- | --- |
| Day 1 | = IF( <= 0.125 x Current RAS, print(), ELSE(print(0.125 x Current RAS)) |
| Day 2 | = IF( – Day1 <= 0.125 x (Current RAS + Day1), print( – Day1), ELSE(print(0.125 x (Current RAS + Day1)) |
| Day 3 | = IF( – Day1 – Day2 <= 0.125 x (Current RAS + Day1 + Day2), print( – Day1 – Day2),ELSE(print(0.125 x (Current RAS + Day1 + Day2)) |
| Day 4 | = IF( – Day1 – Day2 – Day 3 <= 0.125 x (Current RAS + Day1 + Day2 + Day3), print( – Day1 – Day2 – Day3), ELSE(print(0.125 x (Current RAS + Day1 + Day2 + Day3)) |
| Day 5 | = IF( – Day1 – Day2 – Day 3 – Day4 <= 0.125 x (Current RAS + Day1 + Day2 + Day3 + Day4), print( – Day1 – Day2 – Day3 – Day4), ELSE(print(0.125 x (Current RAS + Day1 + Day2 + Day3 + Day4)) |
| Day 6 | = IF( – Day1 – Day2 – Day 3 – Day4 – Day5 <= 0.125 x (Current RAS + Day1 + Day2 + Day3 + Day4 + Day5), print( – Day1 – Day2 – Day3 – Day4 – Day5), ELSE(print(0.125 x (Current RAS + Day1 + Day2 + Day3 + Day4 + Day5)) |
| Day 7 | = IF( – Day1 – Day2 – Day 3 – Day4 – Day5 – Day6 <= 0.125 x (Current RAS + Day1 + Day2 + Day3 + Day4 + Day5 + Day6), print( – Day1 – Day2 – Day3 – Day4 – Day5 – Day6), ELSE(print(0.125 x (Current RAS + Day1 + Day2 + Day3 + Day4 + Day5 + Day6)) |
| Day 8 | = IF( – Day1 – Day2 – Day 3 – Day4 – Day5 – Day6 – Day7 <= 0.125 x (Current RAS + Day1 + Day2 + Day3 + Day4 + Day5 + Day6 + Day7), print( – Day1 – Day2 – Day3 – Day4 – Day5 – Day6 – Day7), ELSE(print(0.125 x (Current RAS + Day1 + Day2 + Day3 + Day4 + Day5 + Day6 + Day7)) |
| Day 9 | = IF( – Day1 – Day2 – Day 3 – Day4 – Day5 – Day6 – Day7 – Day8 <= 0.125 x (Current RAS + Day1 + Day2 + Day3 + Day4 + Day5 + Day6 + Day7 + Day8), print( – Day1 – Day2 – Day3 – Day4 – Day5 – Day6 – Day7 – Day8), ELSE(print(0.125 x (Current RAS + Day1 + Day2 + Day3 + Day4 + Day5 + Day6 + Day7 + Day8)) |
| Day 10 | = IF( – Day1 – Day2 – Day 3 – Day4 – Day5 – Day6 – Day7 – Day8 – Day9 <= 0.125 x (Current RAS + Day1 + Day2 + Day3 + Day4 + Day5 + Day6 + Day7 + Day8 + Day9), print( – Day1 – Day2 – Day3 – Day4 – Day5 – Day6 – Day7 – Day8 – Day9), ELSE(print(0.125 x (Current RAS + Day1 + Day2 + Day3 + Day4 + Day5 + Day6 + Day7 + Day8 + Day9)) |