S2_WAS : Formulae

Cover Sheet: There are five methods (MCRT, SRT, MLSS, F/M Ratio, Yield) used to compute WAS. In this sheet, the user selects the appropriate method as per their choice.

A. WAS_MCRT:

Target WAS:

If able to get from Facility Datasheet

INPUTS:

- Design or Target MCRT = Facility Datasheet - Inputs: 
Design MCRT (includes solids in clarifier)

- F(SCw) = Facility Datasheet - Outputs: 
Total Flow leaving Secondary Clarifier Weirs (F(SCw)

- Current Secondary WAS Flow = Facility Datasheet - Inputs: 
Secondary WAS Flow (F(WASs))

- C(RAS) = Facility Datasheet - Inputs: 
Avg. RAS concentration (C(RAS))

- C(DL) = T&V_TSS - Results: Weekly Discharge Limit

- Solids inventory AB = Facility Datasheet - Outputs: 
Solids Inventory, Aeration Basins (SI(AB))

- Solids inventory SC = Facility Datasheet - Outputs: 
Solids Inventory, Secondary Clarifiers (SI(SC))

- T(WASs) = Facility Datasheet - Inputs: 
Minutes of operation of Secondary WAS pump per hour, on average (T(WASs))

OUTPUTS: 
Target F(WASs) in GPM as per above formula. Then use the following unit conversion table.

| GPM to GPD | GPD to MGD |
| --- | --- |
| GPD = GPM . T(WASs) . 24 | MGD = GPD . 10^-6 |

If unable to get from Facility Datasheet

INPUTS: User inputs for fields mentioned in WAS_MCRT sheet.

OUTPUTS:

Solids Inventory, AB = Use formula provided:

Solids Inventory, Aeration Basin (SIAB) = VAB . CMLSS . 8.34

Solids Inventory, SC = Use formula provided:

Solids Inventory, Secondary Clarifiers (SISC) 
= VSC . {(CMLSS + CRAS) / 2} . {(DSC – DB) / DSC} . 8.34

Add Solids Inventory from both AB and SC in the above formula.

Target F(WASs) in GPM as per above formula. Then use the following unit conversion table.

| GPM to GPD | GPD to MGD |
| --- | --- |
| GPD = GPM . T(WASs) . 24 | MGD = GPD . 10^-6 |

WAS_SRT:

Target WAS:

If able to get from Facility Datasheet

INPUTS:

- Design or Target SRT = Facility Datasheet - Inputs: 
Design SRT (includes solids in clarifier)

- F(SCw) = Facility Datasheet - Outputs: 
Total Flow leaving Secondary Clarifier Weirs (F(SCw)

- Current Secondary WAS = Facility Datasheet - Inputs: 
Secondary WAS Flow (F(WASs))

- C(RAS) = Facility Datasheet - Inputs: 
Avg. RAS concentration (C(RAS))

- Solids inventory, AB = Source: Facility Datasheet - Outputs: 
Solids Inventory, Aeration Basins (SI(AB))

- C(DL) = T&V_TSS - Results: 
Weekly Discharge Limit

- T(WASs) = Facility Datasheet - Inputs: 
Minutes of operation of Secondary WAS pump per hour, on average (T(WASs))

OUTPUTS:

Target F(WASs) in GPM as per above formula. Then use the following unit conversion table.

| GPM to GPD | GPD to MGD |
| --- | --- |
| GPD = GPM . T(WASs) . 24 | MGD = GPD . 10^-6 |

If unable to get from Facility Datasheet

INPUTS: User inputs for fields mentioned in WAS_SRT sheet.

OUTPUTS:

Solids inventory, AB = Use formula provided.

Solids Inventory, Aeration Basin (SIAB) = VAB . CMLSS . 8.34

Target F(WASs) in GPM as per above formula. Then use the following unit conversion table.

| GPM to GPD | GPD to MGD |
| --- | --- |
| GPD = GPM . T(WASs) . 24 | MGD = GPD . 10^-6 |

WAS_MLSS:

Target WAS:

If able to get from Facility Datasheet

INPUTS:

- Design or Target MLSS = Facility Datasheet - Inputs: 
Design or Target MLSS

- F(WASs) : Current Secondary WAS Flow = Facility Datasheet - Inputs:

Secondary WAS Flow (F(WASs))

- C(RAS) = Facility Datasheet - Inputs: 
Avg. RAS concentration (C(RAS))

- Actual Solids, AB = Facility Datasheet - Outputs: 
Solids Inventory, Aeration Basins (SI(AB))

- Actual Solids, SC = Facility Datasheet - Outputs: 
Solids Inventory, Secondary Clarifiers (SI(SC))

- T(WASs) = Facility Datasheet - Inputs: 
Minutes of operation of Secondary WAS pump per hour, on average (T(WASs))

OUTPUTS:

Target Solids Inventory, Aeration Basin as per the following formula:

= VAB . DesignMLSS . 8.34

Target Solids Inventory, Secondary Clarifiers as per the following formula:

= VSC . {(DesignMLSS + CRAS) / 2} . {(DSC – DB) / DSC} . 8.34 . 10-6

Combined Inventory = Aeration Basins Inventory + Secondary Clarifiers Inventory

Target F(WASs) in GPM as per above formula. Then use the following unit conversion table.

| GPM to GPD | GPD to MGD |
| --- | --- |
| GPD = GPM . T(WASs) . 24 | MGD = GPD . 10^-6 |

If unable to get from Facility Datasheet

INPUTS: User inputs for fields mentioned in WAS_MLSS sheet.

OUTPUTS:

Actual Solids inventory, AB = Use formula provided:

Solids Inventory, Aeration Basin (SIAB) = VAB . CMLSS . 8.34

Actual Solids inventory, SC = Use formula provided:

Solids Inventory, Secondary Clarifiers (SISC) = FWASs . TWASs . CRAS . 24 . 8.34 . 10-6

Target Solids Inventory, Aeration Basin as per the following formula:

= VAB . DesignMLSS . 8.34

Target Solids Inventory, Secondary Clarifiers as per the following formula:

= VSC . {(DesignMLSS + CRAS) / 2} . {(DSC – DB) / DSC} . 8.34 . 10-6

Combined Inventory = Aeration Basins Inventory + Secondary Clarifiers Inventory

Target F(WASs) in GPM as per above formula. Then use the following unit conversion table.

| GPM to GPD | GPD to MGD |
| --- | --- |
| GPD = GPM . T(WASs) . 24 | MGD = GPD . 10^-6 |

WAS_FM:

Target WAS:

If able to get from Facility Datasheet

INPUTS:

- Target FM = Facility Datasheet - Inputs: 
Design or Target F/M Ratio

- Current F(WASs) = Source: Facility Datasheet - Inputs: 
Secondary WAS Flow (F(WASs))

- Actual FM = Facility Datasheet - Outputs: 
F/M Ratio (FM)

- F(AB) = Facility Datasheet - Outputs: 
Total Flow entering Aeration Basins (F(AB))

- F(WASs) : Current Secondary WAS Flow = Facility Datasheet - Inputs: 
Secondary WAS Flow (F(WASs))

- C(RAS) = Facility Datasheet - Inputs: 
Avg. RAS concentration (C(RAS))

- T(WASs) = Facility Datasheet - Inputs: 
Minutes of operation of Secondary WAS pump per hour, on average (T(WASs))

OUTPUTS:

Target F(WASs) in GPM as per above formula. Then use the following unit conversion table.

| GPM to GPD | GPD to MGD |
| --- | --- |
| GPD = GPM . T(WASs) . 24 | MGD = GPD . 10^-6 |

If unable to get from Facility Datasheet

INPUTS: User inputs for fields mentioned in WAS_FM sheet.

OUTPUTS:

Actual FM as per the following formula:

= QBODi / QMLVSS = (FAB . CBODi . 8.34) / (VAB . CMLVSS . 8.34)

Target F(WASs) in GPM as per above formula. Then use the following unit conversion table.

| GPM to GPD | GPD to MGD |
| --- | --- |
| GPD = GPM . T(WASs) . 24 | MGD = GPD . 10^-6 |

WAS_Yield:

Target WAS:

If able to get from Facility Datasheet

INPUTS:

- Y = Yield Coefficient (User Input)

- F(AB) = Facility Datasheet - Outputs: 
Total Flow entering Aeration Basins (F(AB))

- F(SCw) = Facility Datasheet - Outputs: 
Total Flow leaving Secondary Clarifier Weirs (F(SCw)

- Current Secondary WAS Flow = Source: Facility Datasheet - Inputs: 
Secondary WAS Flow (F(WASs))

- C(BODi) = Facility Datasheet - Inputs: 
Avg. BOD concentration in Aeration Basin Influent (C(BODi))

- C(BODw) = Facility Datasheet - Inputs: 
Avg. BOD concentration at Weirs of Secondary Clarifiers (C(BODw))

- C(DL) = T&V_TSS - Results: 
Weekly Discharge Limit

- C(RAS) = Facility Datasheet - Inputs: 
Avg. RAS concentration (C(RAS))

- T(WASs) = Source: Facility Datasheet - Inputs: 
Minutes of operation of Secondary WAS pump per hour, on average (T(WASs))

OUTPUTS:

Target F(WASs) in GPM as per above formula. Then use the following unit conversion table.

| GPM to GPD | GPD to MGD |
| --- | --- |
| GPD = GPM . T(WASs) . 24 | MGD = GPD . 10^-6 |

If not able to get from Facility Datasheet

INPUTS: User inputs for fields mentioned in WAS_FM sheet.

OUTPUTS:

Target F(WASs) in GPM as per above formula. Then use the following unit conversion table.

| GPM to GPD | GPD to MGD |
| --- | --- |
| GPD = GPM . T(WASs) . 24 | MGD = GPD . 10^-6 |

Remaining Steps similar to RAS (common to all five methods):

- Required Change in Secondary WAS Flow = 
Target Secondary WAS Flow - Current Secondary WAS Flow

The difference can be either (+) or (–). If (+) the operator has to increase WAS flow, If (–) the operator has to decrease WAS flow

- The increase or decrease cannot be more than 12.5% per day. Therefore, day-by-day schedule of flow changes is prepared as follows:

| Day | Required Flow Change (+) or (-), Applies to all Qw(MGD), Qw(GPD), Qw(GPM) |
| --- | --- |
| Day 1 | = IF( <= 0.125 x Current WAS, print(), ELSE(print(0.125 x Current WAS)) |
| Day 2 | = IF( – Day1 <= 0.125 x (Current WAS + Day1), print( – Day1), ELSE(print(0.125 x (Current WAS + Day1)) |
| Day 3 | = IF( – Day1 – Day2 <= 0.125 x (Current WAS + Day1 + Day2), print( – Day1 – Day2),ELSE(print(0.125 x (Current WAS + Day1 + Day2)) |
| Day 4 | = IF( – Day1 – Day2 – Day 3 <= 0.125 x (Current WAS + Day1 + Day2 + Day3), print( – Day1 – Day2 – Day3), ELSE(print(0.125 x (Current WAS + Day1 + Day2 + Day3)) |
| Day 5 | = IF( – Day1 – Day2 – Day 3 – Day4 <= 0.125 x (Current WAS + Day1 + Day2 + Day3 + Day4), print( – Day1 – Day2 – Day3 – Day4), ELSE(print(0.125 x (Current WAS + Day1 + Day2 + Day3 + Day4)) |
| Day 6 | = IF( – Day1 – Day2 – Day 3 – Day4 – Day5 <= 0.125 x (Current WAS + Day1 + Day2 + Day3 + Day4 + Day5), print( – Day1 – Day2 – Day3 – Day4 – Day5), ELSE(print(0.125 x (Current WAS + Day1 + Day2 + Day3 + Day4 + Day5)) |
| Day 7 | = IF( – Day1 – Day2 – Day 3 – Day4 – Day5 – Day6 <= 0.125 x (Current WAS + Day1 + Day2 + Day3 + Day4 + Day5 + Day6), print( – Day1 – Day2 – Day3 – Day4 – Day5 – Day6), ELSE(print(0.125 x (Current WAS + Day1 + Day2 + Day3 + Day4 + Day5 + Day6)) |
| Day 8 | = IF( – Day1 – Day2 – Day 3 – Day4 – Day5 – Day6 – Day7 <= 0.125 x (Current WAS + Day1 + Day2 + Day3 + Day4 + Day5 + Day6 + Day7), print( – Day1 – Day2 – Day3 – Day4 – Day5 – Day6 – Day7), ELSE(print(0.125 x (Current WAS + Day1 + Day2 + Day3 + Day4 + Day5 + Day6 + Day7)) |
| Day 9 | = IF( – Day1 – Day2 – Day 3 – Day4 – Day5 – Day6 – Day7 – Day8 <= 0.125 x (Current WAS + Day1 + Day2 + Day3 + Day4 + Day5 + Day6 + Day7 + Day8), print( – Day1 – Day2 – Day3 – Day4 – Day5 – Day6 – Day7 – Day8), ELSE(print(0.125 x (Current WAS + Day1 + Day2 + Day3 + Day4 + Day5 + Day6 + Day7 + Day8)) |
| Day 10 | = IF( – Day1 – Day2 – Day 3 – Day4 – Day5 – Day6 – Day7 – Day8 – Day9 <= 0.125 x (Current WAS + Day1 + Day2 + Day3 + Day4 + Day5 + Day6 + Day7 + Day8 + Day9), print( – Day1 – Day2 – Day3 – Day4 – Day5 – Day6 – Day7 – Day8 – Day9), ELSE(print(0.125 x (Current WAS + Day1 + Day2 + Day3 + Day4 + Day5 + Day6 + Day7 + Day8 + Day9)) |