S4_Alkali Dosing: Formulae

- Total Alkinity Required (lbs/d)=Qi .8.34 . (AlkN+80)

where, AlkN (mg/L)= 8 . NH3Ni

AlkN : Alkalinity required for nitrification (mg/L)

NH3-Ni : Ammoniacal Nitrogen conc in Influent to Aeration Basin

Qi : Influent flow rate to Aeration Basin = Primary Effluent – Diverted Flow

- Alkali Dosing Reqd (lbs/d)= Total Alk Reqd-(Qi .8.34 . Influent Alk)

where,

Influent Alk : CaCO3 concentration in Aeration Basin influent (mg/L)x

- IF(Alkali Dosing Reqd <= 0, print(No alkali dosing required)

ELSE, user selects dosing chemical from 3 options as follows:

Lime Slurry (commercial grade: 30%)

Caustic Soda (commercial grade: 50%)

Magnesium hydroxide (commercial grade: 60%)

- IFS(User selects :

Lime Slurry (commercial grade: 30%), then Alk produced=3.6 lbs/gal

Caustic Soda (commercial grade: 50%), then Alk produced=7.43 lbs/gal

Magnesium hydroxide (commercial grade: 60%), then Alk produced=13.38 lbs/gal

- Alkali Dosing Reqd GPD or gal/d=Alkali Dosing Reqd (lbs/d)Alk produced (lbs/gal)

- Alkali Dosing Reqd GPM orgalmin=Alkali Dosing Reqd (GPD or gal/d)Minutes of operation per hour of dosing pump .  24

- Alkali Dosing Reqd mL/min= Alkali Dosing Reqd GPM orgalmin . 3785.41