S6_Nutrient Dosing: Formulae

- Nutrient proportions, CBODi :N :P :Fe=100 :5 :1 :0.5

where, CBODi = Avg BOD concentration in Aeration Basin influent (mg/L or ppm)

Therefore,

Total Nitrogen (TN) requirement = CBODi / 20

Total Phosphorus (TP) requirement = CBODi /100

Iron (Fe) requirement = CBODi / 200

Apart from the above, some residual conc. in AB effluent should also be maintained.

- Total N requirement (mg/L or ppm)=CBODi20+1.0

- Total P requirement (mg/L or ppm)=CBODi100+0.5

- Total Fe requirement (mg/L or ppm)=CBODi200+0.1

- IF(Total N / P / Fe requirement (mg/L or ppm) > 
corresponding Avg. N / P / Fe concentration in Aeration Basin influent (mg/L or ppm), 
print(More N/P/Fe required. Refer below for dosing amounts.)
ELSE print(N/P/Fe is sufficient. No dosing required.)

- Three suggested dosing chemicals for N, P, Fe are recommended along with densities:

| Chemical | % Purity | MW Ratio | Density (lbs/gal) |
| --- | --- | --- | --- |
| Anhydrous Ammonia, (for N) | 80 | 17/14 | 6.34 |
| Trisodium phosphate, (for P) | 75 | 164/31 | 18.00 |
| Ferric chloride, (for Fe) | 39 | 162.5/56 | 11.93 |

| Recommended Nutrient Dosing Rates | GPD | GPM | mL/min |
| --- | --- | --- | --- |
| Anhydrous Ammonia, commercial grade 80% | See below | = GPD / (24 . Mins of op. of Nutrient dosing pump per hr, on avg) | = GPM . 3785.41 |
| Trisodium phosphate, commercial grade 75% |  |  |  |
| Ferric chloride, commercial grade 39% |  |  |  |

IF(Total N / P / Fe requirement (mg/L or ppm) > 
corresponding Avg. N / P / Fe concentration in Aeration Basin influent (mg/L or ppm), 
apply GPD formula below
ELSE(=0)

GPD formula: 
(Total nutrient requirement - Avg nutrient concentration in AB inf) . FAB . 8.34 . (100/Purity) . MW Ratio . (1/Density)

where,

FAB : Total Flow to Aeration Basins, including RAS (MGD)