S7_Polymer Dosing: Formulae

Chemical Selection: User enters Chemical, Solid/Liquid state, % purity, Specific Gravity
Amount of dry polymer per gal (lbs/gal)=8.34 . % Purity100.  Specific Gravity

- Preparing the Stock Solution

- User enters the desired concentration in stock solution in %, if known OR

- User selects the desired range of dosage (mg/L) from the table (or dropdown list). Based on the selection, the corresponding concentration value in mg/L and % are used in the calculation.

| Polymer Dosage Range (mg/L) | Stock Soln conc (mg/L) | Stock Soln conc (%) |
| --- | --- | --- |
| 1-10 | 1000 | 0.1 |
| 10-50 | 10,000 | 1.0 |
| 50-500 | 100,000 | 10 |

- For solid (dry) material,

IF(user selects ‘Liquid’, print (N/A),

ELSE(print(Recommendation :

Dissolve Stock soln conc (mg/L) .  Vol of stock solution (mL)106 grams of chemical in

<Vol of stock solution> mL of distilled water to prepare

<Desired % concentration> of stock solution.

- For liquid material,
IF(user selects ‘Solid (dry)’, print (N/A),
ELSE(print(Recommendation :
Take Stock soln conc (%) .  Vol of stock solution (mL)(% Purity/100) .  Specific Gravity mL of the chemical and dilute with distilled water upto <Vol of stock solution> mL of distilled water to prepare

<Desired % concentration> of stock solution.

Dosing Rate:

IF(user provides Desired Dosage Concentration. (mg/L), then
Polymer dosing reqd lbsd=Qi MGD . Desired Dosage Conc (mgL) . 8.34

ELSE(user provides Desired Dosage in mL, thenPolymer dosing reqd lbsd=Qi MGD .Stock soln conc (mg/L).Desired Dosage (mL)Vol of stock solution (mL) . 8.34

where,

Qi : Influent flow to Aeration Basin (MGD) = Primary Effluent Flow – Diverted Flow

- Polymer dosing reqd GPD or gal/d=Polymer dosing reqd (lbs/d)Amt of dry polymer per gal (lbs/gal)

- Polymer dosing reqd GPM orgalmin=Polymer dosing reqd (GPD or gal/d)Minutes of operation per hour of dosing pump .  24

- Polymer dosing reqd mL/min= Polymer dosing reqd galmin . 3785.41