S5_Chlorine Dosing: Formulae

- Chlorine Dosing Required (lbs/d)=6 . Solids Inventory AB+SC .  MLVSS to MLSS Ratio 1000

where,

Solids Inventory AB+SC : 
Solids inventory in Aeration Bank + Solids inventory in Secondary Clarifiers (apply from Facility datasheet)

- User selects dosing chemical of choice from three options as follows:

Sodium hypochlorite (NaOCl) 5.25%

Sodium hypochlorite (NaOCl) 10.0%

Sodium hypochlorite (NaOCl) 12.5%

Sodium hypochlorite (NaOCl) 15.0%

- IFS(User selects :

Sodium hypochlorite (NaOCl) 5.25%, then Cl produced=0.44 lbs/gal

Sodium hypochlorite (NaOCl) 10.0%, then Cl produced=0.83 lbs/gal

Sodium hypochlorite (NaOCl) 12.5%, then Cl produced=1.00 lbs/gal

Sodium hypochlorite (NaOCl) 15.0%, then Cl produced=1.25 lbs/gal

- Chlorine Dosing Required (GPD or gal/d)=Chlorine Dosing Reqd (lbs/d)Chlorine produced (lbs/gal)

- Chlorine Dosing Reqd GPM orgalmin=Chlorine Dosing Reqd (GPD or gal/d)Minutes of operation per hour of dosing pump .  24

- Chlorine Dosing Reqd mL/min= Chlorine Dosing Reqd galmin . 3785.41

- Frequency of exposure=ROUNDUPRAS solids pumped per daySolids inventory AB+SC

where, RAS solids pumped per day=RAS flow rate MGD. RAS concmgL . 8.34

IFS(
Frequency of exposure >= 3, print(Set up your pump to dose ___ mL/min of ___ (selected chemical)),

Frequency of exposure < 3, print(You need more application points to dose the RAS. Set up two or more pumps to collectively dose ___ mL/min of ___ (selected chemical))