S8_Odor Control: Formulae

- Amount of H2S (lbs/d) in wastewater=Qi . H2S conc . 8.34

where,

Qi : Influent flow to Aeration Basin (MGD) = Primary Effluent Flow – Diverted Flow

H2S conc : H2S concentration (mg/L) in Aeration Basin influent

- Suggested chemicals with H2S oxidation ability Densities as follows:

| Chemical | Oxidation ability (lbs of chemical reqd per lb H2S) | Density (lbs/gal) |
| --- | --- | --- |
| Hydrogen Peroxide (H2O2) 50% purity | 2.0 | 10.01 |
| Potassium Permanganate (KMnO4), 97% purity, neutral pH | 4.0 | 22.13 |
| Potassium Permanganate (KMnO4), 97% purity, neutral pH | 13.0 | 22.13 |

- Dosage required (lbs/d)=Amount of H2S (lbs/d) .  H2S ox ability (lbs/lb H2S)

- Dosage required GPD or gal/d=Dosage required (lbs/d)Density (lbs/gal)

- Dosage required GPM or gal/min=Dosage required (GPD or gal/d)Minutes of operation per hour of dosing pump .  24

- Dosage required mL/min= Dosage required GPM or gal/min . 3785.41