TSS

This page details all you need to know about Monitoring for TSS (Total Suspended Solids).

TSS, MLSS, MLVSS Measurement Techniques:

You need to monitor for TSS at different locations in your facility, starting with the effluent channel before final discharge. Monitoring for TSS systematically at locations upstream from there on, gives a good indication of the source of the problem and malfunctioning or underperforming treatment units or stages.

TSS can be monitored and measured in three ways :

- Digital measurement - TSS sensors or monitors

- Lab Test (Gravimetric Filtration) - Standard Methods 2540 D, APHA

- Decanter Centrifuge

These are explained in further detail below. Choose the method that works for you.

TVSS (Total Volatile Suspended Solids) or MLVSS (Mixed Liquor Volatile Suspended Solids) measurement is described subsequently (scroll further below).

- Digital measurement - TSS sensors or monitors

About this method:

- There are portable, hand-held meters, sensors, monitors and analyzers available in the market for measuring TSS and a host of other polluting parameters.

- Advantages: Accurate, Saves time and money in the long run, considering TSS is a critical parameter you have to keep monitoring regularly.

- Disadvantages: Electronic device might malfunction, probes could lose sensitivity, require calibration, etc.

Procedure:

- Make sure your probes are rinsed and dried before use. Monitor for TSS at a handful of locations in the vicinity. The readings shouldn't fluctuate (change) too much. Your monitoring locations should have :

  - Well-mixed water (the water looks uniform)

  - Steady flow, not violent (turbulent)

  - No accumulation (build-up) of sediments

Precautions / Sources of Error:

- Make sure to test for TSS correctly as described above. The monitoring location must be uniform (homogenous), so it can be representative.

- Keep the probes clean. Rinse and dry them regularly.

- Check the technical manual for guidance on maintenance and calibration.

Final Calculation:

Read from meter.

Report as TSS or MLSS (for Aeration Basins) : ______ mg/L

- Lab Test (Gravimetric Filtration) - 
Standard Methods 2540D, APHA ; USGS I-3765-85; EPA Method 160.2

About this method:

- The sample (whole bottle sample or well mixed sub-sample) is filtered, with rinsing, through a pre-weighed glass fiber filter, and the residue on the filter is dried to constant weight at 103-105℃.

- Advantages: Established method, Cheaper

- Disadvantages: More chances of error, Takes more time and effort

Procedure:

- Sampling : Make sure your sampling containers are rinsed, dried and labelled before use. Monitor for TSS at a handful of locations in the vicinity. Your monitoring locations should have :

  - Well-mixed water (the water looks uniform)

  - Steady flow, not violent (turbulent)

  - No accumulation (build-up) of sediments

- Apparatus & Materials required : Sampling containers, Glass-fiber filter, Wide-bore pippet, Graduated cylinder, Forceps, Dessicator, Convection Oven, Vacuum suction flask, Analytical Balance, Distilled or Deionized water

- Method:

- Pre-wash glass fiber filters (nominal 1.5 μm pore size) with de-ionized water, bake at 103- 105°C (or hotter) for at least 1 hour, and pre-weigh using an analytical balance.

- Make the water samples uniform by vigorously mixing well just before sub-sampling (or use whole bottle if whole bottle sampling is requested).

- Accurately measure the required sample volume, and transfer to a filtration apparatus containing a pre-weighed filter.

- Rinse filter with 3 volumes of 10 mL deionized water, or as-required to ensure full rinsing of dissolved salts from all portions of the filter paper using the selected apparatus.

- Dry the filter to constant weight in an oven at 103° - 105°C for 24 hours. Remove and cool inside a dessicator.

- Accurately measure the post-weight of the filter. Report the mass increase of the filter per litre of sample as TSS (mg/L).

For NPDES or CWA reporting, consult Standard Methods for the Examination of Water and Wastewater, 2540D or USGS I-3765-85 or EPA Method 160.2.

Precautions / Sources of Error:

- Make sure to sample for TSS correctly as described above. The monitoring location must be uniform (homogenous), so it can be representative.

- Make sure your containers and appartus are always cleaned, rinsed with deionized water, and dried before use.

- Sample temperature should be chilled to ≤ 10℃ immediately after sampling and during transit to the laboratory. In the laboratory, samples must be refrigerated at ≤ 6℃. Avoid freezing to prevent sample breakage.

- Choosing the right filter : Filtration must utilize a glass fiber filter with nominal pore size of ~ 1.5 μm, e.g. using filters such as Whatman 934AH, Gelman A/E, Millipore AP40, Ahlstrom 161, Environmental Express Pro Weigh, or equivalent.

- Drying of filters must be conducted at 103 - 105℃.

- Make sure to transfer the effluent sample gently between appartus.

- Make sure your vacuum suction flask is functioning consistently well.

- Identify any sample that yields a residue mass < 2.5 mg or > 200 mg and report the results as an “estimate” because the mass has exceeded the criteria of this analysis.

Final Calculation:

TSS (mg/L) = (W2 - W1) (mg) x 1000 / V (L)

where,

W2 = final 103-105℃ weight of the dried residue + the tared filter, in milligrams (mg)

W1 = tared filter weight, in milligrams (mg)

V = Sample volume in Litres (L).

Report as TSS or MLSS (for Aeration Basins) : ______ mg/L

- Decanter Centrifuge

About this method:

- Centrifugation is a technique used to separate phases of different densities.

- Advantages: Convenient, Fast, Can be used to analyze a large number of samples.

- Disadvantages: Susceptible to errors as accuracy is affected by sludge compactability

Procedure:

- Sampling : Make sure your sampling containers are rinsed, dried and labelled before use. Monitor for TSS at a handful of locations in the vicinity. Your monitoring locations should have :

  - Well-mixed water (the water looks uniform)

  - Steady flow, not violent (turbulent)

  - No accumulation (build-up) of sediments

- Apparatus & Materials required : Sampling container, Centrifuge tubes, Decanter Centrifuge Rotor, Transfer pipette, Conical flasks, Analytical balance

- Method :

  - Draw 15 mL aliquot from a well-mixed container

  - Centrifuge for ten minutes at 2000 or 4000 rpm

  - Pour off supernatant, separating and drying the retained solids

  - Weigh the solids

Precautions / Sources of Error:

- Make sure to sample for TSS correctly as described above. The monitoring location must be uniform (homogenous), so it can be representative.

- Make sure your containers and appartus are always cleaned, rinsed with deionized water, and dried before use.

- Sample temperature should be chilled to ≤ 10℃ immediately after sampling and during transit to the laboratory. In the laboratory, samples must be refrigerated at ≤ 6℃. Avoid freezing to prevent sample breakage.

- Use polypropylene centrifuge tubes with a blue screw cap, not white. Never use glass test tubes.

- Screw on the tube tightly. Check cap for cracks or protrusions.

- Do not fill the centrifuge tube beyond 10 mL.

- When loading your samples into the rotor, ensure it's balances. Tubes of equal weight must be loaded opposite each other. Use water if you don't have another sample to balance the weight.

- Check the technical manual or project guide to know how long the rotor should run, and for guidance on maintenance.

- Don't remove the tubes quickly or shake them violently. Remove the supernatant carefully without disturbing the residue at the bottom.

Final Calculation:

TSS (mg/L) = 4200 x Centrifuge tube reading (mL)

* Note: The conversion factor (K value) of 4200 is an approximate average. You can determine this more accurately by graphing out different MLSS (mg/L) values determined using the other two methods, and different Centrifuge tube readings (mL) to get the exact correlation.

Report as TSS or MLSS (for Aeration Basins) : ______ mg/L

- MLVSS measurement : Standard Methods 208E

About this method:

- This is a gravimetric lab method determines the weight of solids in your wastewater that combust or burn at 550℃. This gives you a rough estimate of the amount or fraction of organic or volatile matter, out of your total suspended solids.

Procedure:

- Follow the same procedure as the gravimetric lab analysis for determining MLSS. Instead of the oven, keep the filter papers inside a muffle furnace, ignited or heated to 550℃ for 1 hour.

For NPDES or CWA reporting, consult Standard Methods for the Examination of Water and Wastewater, 208E

Final Calculation:

TVSS or MLVSS (mg/L) = (W3 - W1) (mg) x 1000 / V (L)

where,

W3 = final 550℃ weight of the dried residue + the tared filter, in milligrams (mg)

W1 = tared filter weight, in milligrams (mg)

V = Sample volume in Litres (L).

Report as TVSS or MLVSS (for Aeration Basins) : ______ mg/L

MLVSS:MLSS Ratio = MLVSS (mg/L) / MLSS (mg/L)