## Locations
ENTER Flow and TSS values for the following Monitoring Locations
Monitoring Location | Flow | TSS conc. | TSS amount | Inference
| MGD | mg/L or ppm | lbs / day | Panel 1 | Panel 2
TSS Discharge Limit : | #REF! | #REF! | #REF! | #REF!
Tertiary Effluent
Tertiary Bypass Sidestream
Tertiary Treatment Stage Outlet
Secondary Effluent |  |  |  | #REF!
Secondary Bypass Sidestream
Filtrate from Sludge Thickening (to tertiary treatment)
Secondary / Final Clarifier Weirs
Secondary / Final Clarifier Center Well
Splitter Box (Distribution Line)
Aeration Basin Outlet - Supernatant
Primary Effluent
RAS
WAS (secondary)
Primary Bypass Sidestream
Filtrate from Sludge Thickening (to secondary treatment)
Primary Clarifier Weirs
Filtrate from Sludge Thickening (to primary treatment)
Raw Influent
WAS (primary)

## Location Codes
# | LOCATION | CODE
1 | Secondary Effluent Stream | L1
2 | Diverted Sidestream (Bypassing Secondary Treatment) | L2
3 | Aeration Basin | L3
4 | Distribution Channel (Aeration Basin Outlet to Splitter Box) | L4
5 | Distribution Channel (Splitter Box to Secondary Clarifier Center Well) | L5
6 | Secondary Clarifier | L6
7 | Primary Treatment Stage | L7
8 | Sludge Handling Operations | L8
9 | Raw Influent | L9

## LOGIC
PROBLEM CODE | VISUAL - 1 : Discharge Limit, Effluent |  |  |  | BACK | NEXT | Visual - 2 : Effluent, Contributing Streams | [6 empty] | BACK | NEXT | Visual - 3 : Contributing Streams, Primary Effluent (or) Raw Influent | [6 empty] | BACK | NEXT | Visual - 4 : Secondary Treatment Investigation : Aeration Basin Supernatant | [5 empty] | BACK | NEXT
| DISPLAY CELLS (in Order specified) | IF | THEN - Display on Panel 1 (Col E) | LOCATIONS for Inspection |  |  | IF-0 (from Datasheet) | DISPLAY CELLS (in Order specified) | IF-1 | THEN - Display on Panel 1 (Col E) | IF-2 | THEN - Display on Panel 2 (Col F) | LOCATIONS for Inspection |  |  | IF-0 (from Datasheet) | DISPLAY CELLS (in Order specified) | IF-1 | THEN - Display on Panel 1 (Col E) | IF-2 | THEN - Display on Panel 2 (Col F) | LOCATIONS for Inspection |  |  | DISPLAY CELLS (in Order specified) | IF-1 | THEN - Display on Panel 1 (Col E) | IF-2 | THEN - Display on Panel 2 (Col F) | LOCATIONS for Inspection
WQSS1 | A1:F3, A4:F4, A5:F5
WQSS2 | A1:F3, A4:F4, A7:F7
WQSS3 | A1:F3, A4:F4, A8:F8 | IF (OR(D4="",D8="")) | < BLANK > |  | 3. Training & Verification > Results Page | >> | IF (AND(Datasheet > Facility > C22 = "Yes"), OR((Datasheet > Facility > C28 = "Tertiary"),(Datasheet > Facility > C28 = "Discharged to Final Effluent")) | A1:F3, A8:F8, A11:F11, A9:F10 |  | "&D11*100/D8&" % of solids in the final effluent are from the secondary treatment unit. "&D9*100/D8&" % of solids in the final effluent are from the diverted sidestream. "&D10*100/D8&" % of solids in the final effluent are from sludge dewatering. | NESTED IF(SUM(D9:D11) < 0.95*D8) | Your effluent has got more solids than what's going into it. This means : 1. There's a slug discharge (spill) downstream, (and/or) 2. You might have to check your readings, or redo the monitoring. | Secondary Effluent Line | << | >> | IF (Datasheet > Facility > C25 = "Primary Effluent") | A1:F3, A11:F11, A9:F10, A15:F15 | NESTED IF((D15 - D11)*100 / D15) >= 80 | Your secondary treatment unit is removing "&(D15 - D11)*100 / D15&" % of solids entering it. | NON-NESTED IF(C9>C15) | Your sidestream from the primary effluent has got more solids than what's going into it. This means : 1. There's a slug discharge (spill) in the sidestream, (and/or) 2. You might have to check your readings, or redo the monitoring. | Sidestream bypassing secondary treatment | << | >> | Skip to Visual - 5 (Secondary Treatment Efficiency > 80%) | [5 empty] | << | >>
[11 empty] | ELSE |  | Filtrate line from sludge dewatering, to final effluent |  |  |  |  | ELSE | Your secondary treatment unit is removing "&(D15 - D11)*100 / D15&" % of solids entering it. | ELSE |  |  |  |  | A1:F3, A11:F11, A14:F14, A15:F15 |  | Take a few mixed liquor samples. Allow settling for 60 minutes. Remove supernatant. Measure average TSS of supernatant from the samples. | NESTED AND (IF(C11 > 1.1*C14), C14 <= 0.2*C15) | The Aeration Basin is working fine. The problem is being caused by the distribution channel and/or final clarifiers, which are : 1. Shearing the flocs (and/or) 2. Not allowing enough time for the flocs to settle
[28 empty] | NESTED AND (IF(C11 > 1.1*C14), C14 > 0.2*C15) | A good part of the problem is your distribution channel and/or final clarifiers, which are : 1. Shearing the flocs (and/or) 2. Not allowing enough time for the flocs to settle The Aeration Basin functioning also needs to be looked at.
[28 empty] | NESTED IF(0.9*C14 < C11 < 1.1*C14) | Your bugs aren't forming enough flocs, so there's likely to be a process upset.
[28 empty] | NESTED IF(C11 < 0.9*C14) | Your bugs aren't forming enough flocs, so there's likely to be a process upset. It's unlikely your Aeration Basin supernatant has a lot more TSS than at the Final Clarifier Weirs : 1. Check for errors in your monitoring and testing 2. It's possible your Polymer addition is making up for the bugs not flocking together, but this usually makes a process upset worse!
[16 empty] | IF (Datasheet > Facility > C25 = "Raw Influent") | A1:F3, A11:F11, A9:F10, A22:F22 | NESTED IF((D15 - D11)*100 / D15) >= 80 | Your primary + secondary treatment units, combined are removing "&(D22 - D11)*100 / D22&" % of solids entering the system. | NON-NESTED IF(C9>C22) | Your sidestream from the raw influent has got more solids than what's going into it. This means : 1. There's a slug discharge (spill) in the sidestream, (and/or) 2. You might have to check your readings, or redo the monitoring. | Sidestream bypassing primary treatment |  |  | SKIP to Visual - 5 (since Primary+Secondary Treatment Efficiency > 80%)
[18 empty] | ELSE | Your primary + secondary treatment units, combined are removing "&(D22 - D11)*100 / D22&" % of solids entering the system. | ELSE |  |  |  |  | A1:F3, A11:F11, A14:F14, A15:F15 |  | Take a few mixed liquor samples. Allow settling for 60 minutes. Remove supernatant. Measure average TSS of supernatant from the samples. | NESTED AND (IF(C11 > 1.1*C14), C14 <= 0.2*C15) | The Aeration Basin is working fine. The problem is being caused by the distribution channel and/or final clarifiers, which are : 1. Shearing the flocs (and/or) 2. Not allowing enough time for the flocs to settle
[28 empty] | NESTED AND (IF(C11 > 1.1*C14), C14 > 0.2*C15) | A good part of the problem is your distribution channel and/or final clarifiers, which are : 1. Shearing the flocs (and/or) 2. Not allowing enough time for the flocs to settle The Aeration Basin functioning also needs to be looked at.
[28 empty] | NESTED IF(0.9*C14 < C11 < 1.1*C14) | Your bugs aren't forming enough flocs, so there's likely to be a process upset.
[28 empty] | NESTED IF(C11 < 0.9*C14) | Your bugs aren't forming enough flocs, so there's likely to be a process upset. It's unlikely your Aeration Basin supernatant has a lot more TSS than at the Final Clarifier Weirs : 1. Check for errors in your monitoring and testing 2. It's possible your Polymer addition is making up for the bugs not flocking together, but this usually makes a process upset worse!
|  | IF (C4 >= C8) | Your TSS is within the discharge limit. You might want to recheck your readings. |  | 3. Training & Verification > Results Page | >> | ELIF (Datasheet > Facility > C22 = "Yes") | A1:F3, A8:F8, A11:F11, A9:F9 |  | "&D11*100/D8&" % of solids in the final effluent are from the secondary treatment unit. "&D9*100/D8&" % of solids in the final effluent are from the diverted sidestream. | NESTED IF(SUM(D9,D11) < 0.95*D8) | Your effluent has got more solids than what's going into it. This means : 1. There's a slug discharge (spill) downstream, (and/or) 2. You might have to check your readings, or redo the monitoring. | Secondary Effluent Line | << | >> | IF (Datasheet > Facility > C25 = "Primary Effluent") | A1:F3, A11:F11, A9:F10, A15:F15 | NESTED IF((D15 - D11)*100 / D15) >= 80 | Your secondary treatment unit is removing "&(D15 - D11)*100 / D15&" % of solids entering it. |  |  |  | << | >> | SKIP to Visual - 5 (since Secondary Treatment Efficiency > 80%) | [5 empty] | << | >>
[11 empty] | ELSE | [6 empty] | ELSE | Your secondary treatment unit is removing "&(D15 - D11)*100 / D15&" % of solids entering it. | [5 empty] | A1:F3, A11:F11, A14:F14, A15:F15 |  | Take a few mixed liquor samples. Allow settling for 60 minutes. Remove supernatant. Measure average TSS of supernatant from the samples. | NESTED AND (IF(C11 > 1.1*C14), C14 <= 0.2*C15) | The Aeration Basin is working fine. The problem is being caused by the distribution channel and/or final clarifiers, which are : 1. Shearing the flocs (and/or) 2. Not allowing enough time for the flocs to settle
[28 empty] | NESTED AND (IF(C11 > 1.1*C14), C14 > 0.2*C15) | A good part of the problem is your distribution channel and/or final clarifiers, which are : 1. Shearing the flocs (and/or) 2. Not allowing enough time for the flocs to settle The Aeration Basin functioning also needs to be looked at.
[28 empty] | NESTED IF(0.9*C14 < C11 < 1.1*C14) | Your bugs aren't forming enough flocs, so there's likely to be a process upset.
[28 empty] | NESTED IF(C11 < 0.9*C14) | Your bugs aren't forming enough flocs, so there's likely to be a process upset. It's unlikely your Aeration Basin supernatant has a lot more TSS than at the Final Clarifier Weirs : 1. Check for errors in your monitoring and testing 2. It's possible your Polymer addition is making up for the bugs not flocking together, but this usually makes a process upset worse!
[16 empty] | IF (Datasheet > Facility > C25 = "Raw Influent") | A1:F3, A11:F11, A9:F10, A22:F22 | NESTED IF((D15 - D11)*100 / D15) >= 80 | Your primary + secondary treatment units, combined are removing "&(D22 - D11)*100 / D22&" % of solids entering the system. | [5 empty] | SKIP to Visual - 5 (since Primary+Secondary Treatment Efficiency > 80%)
[18 empty] | ELSE | Your primary + secondary treatment units, combined are removing "&(D22 - D11)*100 / D22&" % of solids entering the system. | [5 empty] | A1:F3, A11:F11, A14:F14, A15:F15 |  | Take a few mixed liquor samples. Allow settling for 60 minutes. Remove supernatant. Measure average TSS of supernatant from the samples. | NESTED AND (IF(C11 > 1.1*C14), C14 <= 0.2*C15) | The Aeration Basin is working fine. The problem is being caused by the distribution channel and/or final clarifiers, which are : 1. Shearing the flocs (and/or) 2. Not allowing enough time for the flocs to settle
[28 empty] | NESTED AND (IF(C11 > 1.1*C14), C14 > 0.2*C15) | A good part of the problem is your distribution channel and/or final clarifiers, which are : 1. Shearing the flocs (and/or) 2. Not allowing enough time for the flocs to settle The Aeration Basin functioning also needs to be looked at.
[28 empty] | NESTED IF(0.9*C14 < C11 < 1.1*C14) | Your bugs aren't forming enough flocs, so there's likely to be a process upset.
[28 empty] | NESTED IF(C11 < 0.9*C14) | Your bugs aren't forming enough flocs, so there's likely to be a process upset. It's unlikely your Aeration Basin supernatant has a lot more TSS than at the Final Clarifier Weirs : 1. Check for errors in your monitoring and testing 2. It's possible your Polymer addition is making up for the bugs not flocking together, but this usually makes a process upset worse!
[7 empty] | ELIF (OR((Datasheet > Facility > C28 = "Tertiary"),(Datasheet > Facility > C28 = "Discharged to Final Effluent"))) | A1:F3, A8:F8, A11:F11, A10:F10 |  | "&D11*100/D8&" % of solids in the final effluent are from the secondary treatment unit. "&D10*100/D8&" % of solids in the final effluent are from sludge dewatering. | NESTED IF(SUM(D10,D11) < 0.95*D8) | [5 empty] | A1:F3, A11:F11, A15:F15 | NESTED IF((D15 - D11)*100 / D15) >= 80 | Your secondary treatment unit is removing "&(D15 - D11)*100 / D15&" % of solids entering it. | [5 empty] | SKIP to Visual - 5 (since Secondary Treatment Efficiency > 80%)
[11 empty] | ELSE |  | Filtrate line from sludge dewatering, to final effluent |  |  |  |  | ELSE | Your secondary treatment unit is removing "&(D15 - D11)*100 / D15&" % of solids entering it. | [5 empty] | A1:F3, A11:F11, A14:F14, A15:F15 |  | Take a few mixed liquor samples. Allow settling for 60 minutes. Remove supernatant. Measure average TSS of supernatant from the samples. | NESTED AND (IF(C11 > 1.1*C14), C14 <= 0.2*C15) | The Aeration Basin is working fine. The problem is being caused by the distribution channel and/or final clarifiers, which are : 1. Shearing the flocs (and/or) 2. Not allowing enough time for the flocs to settle
[28 empty] | NESTED AND (IF(C11 > 1.1*C14), C14 > 0.2*C15) | A good part of the problem is your distribution channel and/or final clarifiers, which are : 1. Shearing the flocs (and/or) 2. Not allowing enough time for the flocs to settle The Aeration Basin functioning also needs to be looked at.
[28 empty] | NESTED IF(0.9*C14 < C11 < 1.1*C14) | Your bugs aren't forming enough flocs, so there's likely to be a process upset.
[28 empty] | NESTED IF(C11 < 0.9*C14) | Your bugs aren't forming enough flocs, so there's likely to be a process upset. It's unlikely your Aeration Basin supernatant has a lot more TSS than at the Final Clarifier Weirs : 1. Check for errors in your monitoring and testing 2. It's possible your Polymer addition is making up for the bugs not flocking together, but this usually makes a process upset worse!
|  | IF (D4 < D8) | You're going over the discharge limit by "&D5-D4&" lbs per day |  | 3. Training & Verification > Results Page | >> | ELSE | A1:F3, A8:F8, A11:F11 |  | "&D11*100/D8&" % of solids in the final effluent are from the secondary treatment unit | NESTED IF(D11 < 0.95*D8) | Your effluent has got more solids than what's going into it. This means : 1. There's a slug discharge (spill) downstream, (and/or) 2. You might have to check your readings, or redo the monitoring. | Secondary Effluent Line | << | >> |  | A1:F3, A11:F11, A15:F15 | NESTED IF((D15 - D11)*100 / D15) >= 80 | Your secondary treatment unit is removing "&(D15 - D11)*100 / D15&" % of solids entering it. |  |  |  | << | >> | SKIP to Visual - 5 (since Secondary Treatment Efficiency > 80%) | [5 empty] | << | >>
[11 empty] | ELSE | [6 empty] | ELSE | Your secondary treatment unit is removing "&(D15 - D11)*100 / D15&" % of solids entering it. | [5 empty] | A1:F3, A11:F11, A14:F14, A15:F15 |  | Take a few mixed liquor samples. Allow settling for 60 minutes. Remove supernatant. Measure average TSS of supernatant from the samples. | NESTED AND (IF(C11 > 1.1*C14), C14 <= 0.2*C15) | The Aeration Basin is working fine. The problem is being caused by the distribution channel and/or final clarifiers, which are : 1. Shearing the flocs (and/or) 2. Not allowing enough time for the flocs to settle
[28 empty] | NESTED AND (IF(C11 > 1.1*C14), C14 > 0.2*C15) | A good part of the problem is your distribution channel and/or final clarifiers, which are : 1. Shearing the flocs (and/or) 2. Not allowing enough time for the flocs to settle The Aeration Basin functioning also needs to be looked at.
[28 empty] | NESTED IF(0.9*C14 < C11 < 1.1*C14) | Your bugs aren't forming enough flocs, so there's likely to be a process upset.
[28 empty] | NESTED IF(C11 < 0.9*C14) | Your bugs aren't forming enough flocs, so there's likely to be a process upset. It's unlikely your Aeration Basin supernatant has a lot more TSS than at the Final Clarifier Weirs : 1. Check for errors in your monitoring and testing 2. It's possible your Polymer addition is making up for the bugs not flocking together, but this usually makes a process upset worse!