Read Me for key understanding (Concept, Target Range, Calculation)

SRT (Solids Retention Time) - BOD removal without Nitrification

- About this test

This document serves as guidance to determine the SRT for BOD removal only, if your facility is not mandated to remove nutrients. Essential information is presented in the form of Q&A in the sections below. In the next page, you will have to enter the average SRT (without nitrification), considering all Aeration Basins and Secondary Clarifiers in service.

- What is SRT?

SRT (Solids Retention Time) is the amount of time, in days, that solids or microorganisms are kept within the activated sludge process before getting wasted. In other words, it is the age of the sludge within your system.

SRT = Solids Inventory (lbs) / Rate of solids leaving secondary treatment (lbs/day)

There are similar other terms like DSRT, CRT, MCRT, Sludge Age. For simplicity, Jarvis will use ‘SRT’ for calculations.

- Why is SRT an important parameter?

- The key to maximizing treatment efficiency is to be able maintain the right quantity of bugs for the influent pollution. For this, new bugs that get produced in the system have to be periodically wasted to the right extent. Maintaining the right SRT indicates you are wasting the right amount of solids for the MLSS concentration.

- Improper SRT through incorrect wasting will affect MLSS concentrations and F/M ratio, and cause process upsets in the form of bulking or foaming episodes.

- What are measurement units of SRT?

SRT is measured in days.

- What is an ideal range of SRT?

BOD removal, without nitrification: 2-8 days

BOD removal and complete nitrification: 4-18 days

The required SRT is shorter in summers due to faster metabolism and longer in winters due to slower metabolism.

The required SRT is longer if you are required to remove ammonia through nitrification-denitrification, as you need to supply oxygen for longer, for complete digestion and nitrification.

Your facility might have a design SRT as target. You could also determine your target SRT through a stepwise calculation, in the subsequent section below.

- How do you calculate your target SRT?

The ideal range of SRT depends on three factors: Wastewater temperature, DO concentration, Target Ammonia concentration in effluent. A sample calculation is provided below:

Assuming:

Temperature of wastewater: 80°F (26.7°C)

DO concentration: 2 mg/L

Wastewater Ammonia concentration: 20 mg/L

(If complete nitrification required) -
Target Ammonia concentration in effluent: 1 mg/L

Step i: Maximum Specific Growth corrected for Temperature : μ(max,T)

μ(max,T) = 0.65 x (1.055)^(T-25)

= 0.65 x (1.055)^(26.7 - 25)

= 0.712

Step ii: Decay Rate corrected for Temperature, k(d)

k(d) = 0.05 x (1.055)^(T-25)

= 0.05 x (1.055)^(26.7 - 25)

= 0.055

Step iii: Growth Rate correction factor for effluent Ammonia : CF(NH4+)

k(N) = 1.0 x (1.055)^(T-25)

= 1.0 x (1.055)^(26.7 - 25)

= 1.095

For BOD removal without nitrification:

CF(NH4) = Effluent Ammonia / ( k(N) + Effluent Ammonia)

= 20 / (1.095 + 20)

= 0.948

For BOD removal with complete nitrification:

CF(NH4) = Effluent Ammonia / ( k(N) + Effluent Ammonia)

= 1 / (1.095 + 1)

= 0.477

Step iv: Growth Rate correction factor for Dissolved Oxygen : CF(DO)

CF(DO) = DO / (1 + DO)

= 2 / (1 + 2)

= 0.667

Step v: Growth Rate corrected for Temperature, Ammonia, DO : μ(T)
	For BOD removal without nitrification:

μ(T) = μ(max,T) x CF(NH4+) x CF(DO), from steps i, iii, iv

= 0.712 x 0.948 x 0.667

= 0.450

For BOD removal with complete nitrification:

μ(T) = μ(max,T) x CF(NH4+) x CF(DO), from steps i, iii, iv

= 0.712 x 0.477 x 0.667

= 0.227

Final step:

For BOD removal without nitrification:

Ideal SRT = 1 / ( μ(T) - k(d) ), from steps ii, v

= 1 / (0.450 - 0.055)

= 2.5

=> 2-3 days

For BOD removal with complete nitrification:

Ideal SRT = 1 / ( μ(T) - k(d) ), from steps ii, v

= 1 / (0.227 - 0.055)

= 5.8

=> 5-6 days

- How do you calculate your current SRT?
Jarvis recommends including solids in Secondary Clarifier within the solids inventory. This is especially important, when the sludge blanket is over 3 ft.

SRT = Solids Inventory (lbs) / Rate of solids leaving secondary treatment (lbs/day)

=>

SRT = (Solids in Aeration Basins + Solids in Secondary Clarifiers)  / 
(Solids leaving through WAS + Solids leaving through secondary effluent)

So the modified formula has four components, each of which is determined through a sample calculation as follows:

Assuming:

Total Volume of Aeration Basins : 0.75 million gal

Total Volume of Secondary Clarifiers : 0.45 million gal

Avg. Depth of Secondary Clarifiers : 14 ft.

Avg. Depth of Sludge Blanket : 11 ft.

Secondary effluent flow rate, on average: 1.2 MGD

Secondary WAS flow rate, on average: 50 GPM or gal/min

Minutes of operation of Secondary WAS pump per hour, on avg.: 25 mins

Note: If are unable to determine Secondary Effluent Flow or Minutes of operation of

WAS pump per hour, on average, a detailed calculation is provided further below.

Avg. MLSS concentration : 3000 mg/L

Avg. RAS concentration : 9000 mg/L

Avg. Secondary Effluent TSS concentration : 40 mg/L

Step i : Solids inventory, Aeration Basins

= Total Volume of Aeration Basins (million gal) x MLSS (mg/L) x 8.34

= 0.75 x 3000 x 8.34

= 18,765 lbs

Step ii : Solids inventory, Secondary Clarifiers

= Total Volume of Secondary Clarifiers (million gal) x Avg. of MLSS, RAS (mg/L)

x Fraction of sludge blanket in clarifier volume x 8.34

= 0.45 x [(3000 + 9000) / 2] x [(14 - 11) / 14)] x 8.34

= 4,825 lbs

Step iii : Solids leaving through WAS

= Sec. WAS flow (GPM) x Mins of op./hr x RAS (mg/L) x 24 x 8.34 / 1,000,000

= 50 x 25 x 9000 x 24 x 8.34 / 1,000,000

= 2,252 lbs/day

Step iv : Solids leaving through Secondary Effluent

= Sec. Effluent Flow (MGD) x Sec. Effluent TSS conc. (mg/L) x 8.34

= 1.2 x 40 x 8.34

= 400 lbs/day

Final step : SRT = Total Solids Inventory / Rate of solids leaving

= (Step i + ii) / (Step iii + iv)

= (18,765 + 4,825) / (2,252 + 400)

= 8.9

=> 8-9 days

Monitoring locations for determining SRT:

- Aeration Basin: Monitoring for Influent flow, MLSS concentration

- Secondary Clarifiers: Monitoring for Effluent flow through weirs, Sludge Blanket

- WAS line: Monitoring for Sludge Wastage rate

- What are factors that affect SRT?

SRT = Solids Inventory (lbs) / Rate of solids leaving secondary treatment (lbs/day)

=>

SRT = (Solids in Aeration Basins + Solids in Secondary Clarifiers)  / 
(Solids leaving through WAS + Solids leaving through secondary effluent)

- As seen in the formula, SRT is affected by several factors:
Numerators:

  - Solids in Aeration Basins:
For the same WAS rate, effluent solids leaving,

    - Higher the MLSS conc. => Higher solids inventory => Higher the SRT and vice versa

    - Higher the Aeration volume => Higher solids inventory => Higher the SRT and vice versa

  - Solids in Secondary Clarifiers: 
For the same WAS rate, effluent solids leaving,

    - Higher the MLSS conc. => Higher solids leaving => Higher the SRT and vice versa

    - Higher the RAS conc. => Higher solids leaving => Higher the SRT and vice versa

    - Higher the Clarifier volume => Higher solids leaving => Higher the SRT and vice versa

    - Thicker the Blanket, higher the SRT and vice versa

Denominators:

  - Solids leaving through WAS:

For the same total solids inventory,

- Higher the WAS flow rate => Higher solids leaving => Lower the SRT and vice versa

- Higher the WAS pump operating time => Higher solids leaving => Lower the SRT and vice versa

- Higher the RAS conc., => Higher solids leaving => Lower the SRT and vice versa

  - Solids leaving through secondary effluent:

For the same total solids inventory,

    - Higher the Secondary Effluent flow rate => Higher solids leaving => Lower the SRT and vice versa

    - Higher the Secondary Effluent TSS conc., => Higher solids leaving => Lower the SRT and vice versa

- Things to keep in mind to ensure accurate calculation of SRT:

- Ensure you account for all flows entering the Aeration Basins and leaving the Secondary Clarifier Weirs

- Ensure your flowmeters are cleaned and calibrated from time to time

- Further corrective actions, if required, will be specified in the Troubleshooting section

- Detailed Calculation of Secondary Effluent Flow, Minutes of operation of WAS pump per hour :

Secondary Effluent Flow, through Clarifier Weirs (MGD) =

FRaw + (FFil . 10-6) – FD – (FWASp . TWASp . 24 . 10-6) – (FWASs . TWASs . 24 . 10-6)

where,

Total flow : Total flow entering Secondary Clarifier (MGD)
	FRaw : Total raw influent flow received by your facility (MGD)

FFil : Filtrate from Sludge thickening, dewatering (GPD or gal per day)

FD : Diverted Sidestream flow bypassing Secondary Treatment (MGD)

FWASp : Primary WAS Flow (GPM or gal per min)

FWASs : Secondary WAS Flow (GPM or gal per min)

TWASp : Minutes of operation of Primary WAS pump per hour, on average

TWASp : Minutes of operation of Secondary WAS pump per hour, on average

Example:
	Raw influent flow (FRaw) = 1.2 MGD

Filtrate from Sludge thickening, dewatering (FFil) = 50,000 GPD

Diverted Sidestream flow bypassing Secondary Treatment (FD) = 0.2 MGD
	Primary WAS Flow (FWASp) = 80 GPM

Secondary WAS Flow (FWASs) = 70 GPM

Minutes of operation of Primary WAS pump per hour (TWASp) = 25

Minutes of operation of Secondary WAS pump per hour (TWASs) = 20

Total flow leaving Secondary Clarifiers, through Clarifier Weirs (MGD) 
	= 1.2 + (50,000 . 10-6) – 0.2 – (80 . 25 . 24 . 10-6) – (70 . 20 . 24 . 10-6)

= 0.97 MGD

Note - if you don’t run your WAS pumps every hour, follow the calculation below:

TWAS (mins/hr) =

Total hours of operation per day x 60 / 24

Total hours of operation per day : 8
	TWAS = 8 x 60 / 24 = 20 mins / hr

- Next step:

In the next page, you will have to input your calculated average SRT (for BOD removal only, without nitrification - if ammonia removal is not mandated per your permit). Consider all Aeration Basins and Secondary Clarifiers in service. Jarvis will use this input to test or check if it’s a sign of a problem within your facility.

- Further Reading:

For a detailed understanding of MLSS - concept, monitoring and calculation, refer to the section below.

Notes on MLSS and MLVSS

- What are MLSS and MLVSS?

- MLSS stands for Mixed Liquor Suspended Solids. This is the average TSS of the water or ‘mixed liquor’ (it is called mixed liquor because of the mixing of the Raw Influent, RAS and the bugs in the reactor).

- MLVSS stands for Mixed Liquor Volatile Suspended Solids. This is the volatile component of MLSS, that is made up of living microorganisms, floating in the water. The rest of the MLSS is inert.

- What’s the difference between TSS, MLSS and MLVSS?

- TSS stands for Total Suspended Solids concentration. It measures the amount of solids floating or suspended (not dissolved) in a certain quantity of water. In other words, it measures the concentration of suspended solids that are over 2 microns in size. TSS could include inert solids like sand and clay, or living (volatile) solids like bacteria and other bugs.

- TSS is the general term, while MLSS refers to the TSS within the Aeration Basins present as mixed liquor.

- MLVSS is the volatile component of MLSS, like VSS is the volatile component of TSS.

- What are measurement units of MLSS and MLVSS?

TSS, MLSS and MLVSS are measured in mg/L or ppm (parts per million).

- How do you measure or calculate MLSS and MLVSS?

MLSS determination:

- Digital measurement - TSS sensors or monitors

- Lab Test (Gravimetric Filtration) - Standard Methods 2540 D, APHA

- Decanter Centrifuge

These are explained in further detail below. Choose the method that works for you.

MLVSS determination:
MLVSS can only be determined using the Lab Test mentioned above, which will be explained further. From the MLSS and MLVSS values, you can determine an average MLVSS / MLSS ratio. If the composition of your total solids is generally stable, you can use the average MLVSS / MLSS ratio in your process calculations, instead of having to measure MLVSS each time.

- Methods to determine MLSS and MLVSS:

I. Digital measurement - TSS sensors or monitors (only MLSS)

About this method:

- There are portable, hand-held meters, sensors, monitors and analyzers available in the market for measuring TSS and a host of other polluting parameters.

- Advantages: Accurate, Saves time and money in the long run, considering TSS is a critical parameter you have to keep monitoring regularly.

- Disadvantages: Electronic device might malfunction, probes could lose sensitivity, require calibration, etc.

Procedure:

- Make sure your probes are rinsed and dried before use. Monitor for TSS at a handful of locations in the vicinity. The readings shouldn't fluctuate (change) too much. Your monitoring locations should have :

  - Well-mixed water (the water looks uniform)

  - Steady flow, not violent (turbulent)

  - No accumulation (build-up) of sediments

Precautions / Sources of Error:

- Make sure to test for TSS correctly as described above. The monitoring location must be uniform (homogenous), so it can be representative.

- Keep the probes clean. Rinse and dry them regularly.

- Check the technical manual for guidance on maintenance and calibration.

Final Calculation:

Read from meter.

Report as TSS or MLSS (for Aeration Basins) : ______ mg/L

II. Lab Test (Gravimetric Filtration) - for MLSS and MLVSS
Standard Methods 2540D, APHA ; USGS I-3765-85; EPA Method 160.2

About this method:

- The sample (whole bottle sample or well mixed sub-sample) is filtered, with rinsing, through a pre-weighed glass fiber filter, and the residue on the filter is dried to constant weight at 103-105℃.

- Advantages: Established method, Cheaper

- Disadvantages: More chances of error, Takes more time and effort

Procedure:

- Sampling : Make sure your sampling containers are rinsed, dried and labeled before use. Monitor for TSS at a handful of locations in the vicinity. Your monitoring locations should have :

  - Well-mixed water (the water looks uniform)

  - Steady flow, not violent (turbulent)

  - No accumulation (build-up) of sediments

- Apparatus & Materials required : Sampling containers, Glass-fiber filter, Wide-bore pipet, Graduated cylinder, Forceps, Dessicator, Muffle Furnace or Convection Oven, Vacuum suction flask, Analytical Balance, Distilled or Deionized water

- Method:

- Pre-wash glass fiber filters (nominal 1.5 μm pore size) with deionized water, bake at 103-105°C (or hotter) for at least 1 hour

- Pre-weigh the filter paper using an analytical balance. Record this weight in mg as M0.

- Make the water samples uniform by vigorously mixing well just before sub-sampling (or use the whole bottle if whole bottle sampling is requested)

- Accurately measure the required sample volume (recommended: 25 mL), and transfer to a filtration apparatus containing a pre-weighed filter. Record this volume in liters as V. For eg, if the volume is 25 mL, record V as 0.025 L.

- Rinse filter with 3 volumes of 10 mL deionized water, or as-required to ensure full rinsing of dissolved salts from all portions of the filter paper using the selected apparatus.

- Leave the filter in the muffle furnace or convection oven at 103° - 105°C for 24 hours.

- Remove and cool inside a dessicator for 15 mins.

- Accurately measure the post-weight of the filter. Record this weight in mg as M1.

- Use the following equation to calculate MLSS in mg/L.

MLSS (mg/L) = (M1 - M0) x 1000 / V
where,
M0 = Weight of tared filter, in mg
M1 = Weight of tared filter, with the dried residue, in mg after heating at 103° - 105°C

V = Volume of sample, in Liters

- Now, set the muffle furnace to 550°C for 2 hours and repeat the steps above. The higher temperature evaporates volatile solids, leaving inserts behind. This time, allow the filter papers to cool in the dessicator for 30 mins.

- Accurately measure the post-weight of the filter. Record this weight in mg as M2.

- Use the following equation to calculate MLVSS in mg/L.

MLVSS (mg/L) = (M1 - M2) x 1000 / V
where,
M1 = Weight of tared filter, with the dried residue, in mg, after heating at 103° - 105°C

M2 = Weight of tared filter, with the dried residue, in mg, after heating at 550°C

V = Volume of sample, in Liters

For NPDES or CWA reporting, consult Standard Methods for the Examination of Water and Wastewater, 2540D or USGS I-3765-85 or EPA Method 160.2.

Precautions / Sources of Error:

- Make sure to sample for TSS correctly as described above. The monitoring location must be uniform (homogenous), so it can be representative.

- Make sure your containers and appartus are always cleaned, rinsed with deionized water, and dried before use.

- Sample temperature should be chilled to ≤ 10℃ immediately after sampling and during transit to the laboratory. In the laboratory, samples must be refrigerated at ≤ 6℃. Avoid freezing to prevent sample breakage.

- Choosing the right filter : Filtration must utilize a glass fiber filter with nominal pore size of ~ 1.5 μm, e.g. using filters such as Whatman 934AH, Gelman A/E, Millipore AP40, Ahlstrom 161, Environmental Express Pro Weigh, or equivalent.

- Drying of filters must be conducted at 103 - 105℃.

- Make sure to transfer the effluent sample gently between appartus.

- Make sure your vacuum suction flask is functioning consistently well.

- Identify any sample that yields a residue mass < 2.5 mg or > 200 mg and report the results as an “estimate” because the mass has exceeded the criteria of this analysis.

III. Decanter Centrifuge

About this method:

- Centrifugation is a technique used to separate phases of different densities.

- Advantages: Convenient, Fast, Can be used to analyze a large number of samples.

- Disadvantages: Susceptible to errors as accuracy is affected by sludge compact-ability

Procedure:

- Sampling : Make sure your sampling containers are rinsed, dried and labelled before use. Monitor for MLSS at a handful of locations in the Aeration Basin. Your monitoring locations should have :

  - Well-mixed water (the water looks uniform)

  - Steady flow, not violent (turbulent)

  - No accumulation (build-up) of sediments

- Apparatus & Materials required : Sampling container, Centrifuge tubes, Decanter Centrifuge Rotor, Transfer pipette, Conical flasks, Analytical balance

- Method :

  - Draw 15 mL aliquot from a well-mixed container

  - Centrifuge for ten minutes at 2000 or 4000 rpm

  - Pour off supernatant, separating and drying the retained solids

  - Weigh the solids

Precautions / Sources of Error:

- Make sure to sample for MLSS correctly as described above. The monitoring location must be uniform (homogenous), so it can be representative.

- Make sure your containers and appartus are always cleaned, rinsed with deionized water, and dried before use.

- Sample temperature should be chilled to ≤ 10℃ immediately after sampling and during transit to the laboratory. In the laboratory, samples must be refrigerated at ≤ 6℃. Avoid freezing to prevent sample breakage.

- Use polypropylene centrifuge tubes with a blue screw cap, not white. Never use glass test tubes.

- Screw on the tube tightly. Check cap for cracks or protrusions.

- Do not fill the centrifuge tube beyond 10 mL.

- When loading your samples into the rotor, ensure it's balanced. Tubes of equal weight must be loaded opposite each other. Use water if you don't have another sample to balance the weight.

- Check the technical manual or project guide to know how long the rotor should run, and for guidance on maintenance.

- Don't remove the tubes quickly or shake them violently. Remove the supernatant carefully without disturbing the residue at the bottom.

Final Calculation:

MLSS (mg/L) = 4200 x Centrifuge tube reading (mL)

* Note: The conversion factor (K value) of 4200 is an approximate average. You can determine this more accurately by graphing out different MLSS (mg/L) values determined using the other two methods, and different Centrifuge tube readings (mL) to get the exact correlation.

Report as MLSS : ______ mg/L