## Sheet1
Enter the Average ORP reading of the wastewater in the Aeration Basin, Outlet End
Sampling Point | Ideal Range | Average ORP in Aeration Basin, Outlet End (mV) | Code
Aeration Basin, Outlet End | 50 - 100 mV
Result Combinations (BACKEND)
Sampling Point | Result | Condition | Code
D : Aeration Basin, Outlet End | Methane Formation in Aeration Basin, Outlet End | Input < -250 | R14.1D
D : Aeration Basin, Outlet End | Septicity, Methane Formation, Phosphorus Release in Aeration Basin, Outlet End | -250 <= Input < -175 | R14.2D
D : Aeration Basin, Outlet End | Septicity, Phosphorus Release in Aeration Basin, Outlet End | -175 <= Input <= -100 | R14.3D
D : Aeration Basin, Outlet End | Denitrification in Aeration Basin, Outlet End | -100 < Input <= 25 | R14.4D
D : Aeration Basin, Outlet End | Phosphorus Removal, Denitrification in Aeration Basin, Outlet End | 25 < Input < 50 | R14.5D
D : Aeration Basin, Outlet End | cBOD Removal, Phosphorus Removal in Aeration Basin, Outlet End | 50 < Input <= 100 | R14.6D
D : Aeration Basin, Outlet End | cBOD Removal, Phosphorus Removal, Nitrification in Aeration Basin, Outlet End | 100 < Input <= 350 | R14.7D
D : Aeration Basin, Outlet End | cBOD Removal, Phosphorus Removal, Nitrification, Chlorine residual in Aeration Basin, Outlet End | 350 < Input | R14.8D