Read Me for key understanding (Concept, Target Range, Calculation)

Hydraulic Retention Time (HRT) - Equalization Basins

- About this test

This document serves as guidance to determine the HRT in your Equalization Basins. Essential information is presented in the form of Q&A in the sections below. In the next page, you will have to enter the average HRT for all Eq basins in service.

- What is HRT?

Hydraulic Retention Time (HRT) is the average time spent by a water molecule, from entry to exit, within a unit.

- Why is HRT an important parameter?

- HRT is basically the time (in hours or days) you allow for the particular unit to perform its physical / chemical / biological function on the wastewater, from the time it enters to its exit. The HRT has to be sufficient enough to ensure your treatment unit’s performance efficiency.

- So, too short HRT can result in reduced treatment effectiveness, while too long HRT can create anaerobic conditions, causing your wastewater to become septic.

- The idea is to provide just enough HRT, so you can keep the flow going and maximize the influent flow you receive.

- How do you calculate HRT?

Refer to the formula and sample calculation below.

HRT (hours) = Volume of unit (million gal) x 24 / Influent flow rate (MGD)

Influent flow rate = 1 MGD (signifies total flow entering Eq basin)
	Volume of Eq basin = 500,000 gal or 0.5 million gal

HRT (hours) = 0.5 x 24 / 1

HRT (hours) = 12

- What are the factors that affect HRT?

HRT (hours) = Volume of unit (million gal) x 24 / Influent flow rate (MGD)

- As seen in the formula, the HRT is affected by the size (volume) of the treatment unit and the speed (rate) of flow.

- For a fixed rate of flow entering a treatment unit, if you increase the size (capacity or volume) of the unit, the HRT increases. Decreasing the capacity decreases the HRT.

- For a fixed treatment capacity, if you slow down the flow, the HRT increases. Speeding up the flow decreases the HRT.

- Your design should provide for the ideal HRT by striking a balance between maximum capacity utilization and maximum influent rate of flow.

- What is the role of Eq basins? How do you ensure their maximum performance?

- Equalization (Eq) Basins equalize the flows received by your facility, to the design flow for the treatment units. Eq basins are essential to regulate variations in flow, especially peak flows, to optimize performance.

- More on Eq Basins and action steps for their effective O&M will be specified in the Troubleshooting section.

- What is the ideal HRT for Eq basins?
12 to 24 hours

- What do you need to keep in mind to ensure you calculate HRT accurately for your Eq basins?

- Ensure you account for all flows entering the Eq basin

- Ensure your flowmeters are cleaned and calibrated from time to time

- Further corrective actions, if required, will be specified in the Troubleshooting section

- Next step:

In the next page, you will have to input the average of your calculated HRT for all Eq basins in service. Jarvis will use this input to test or check if it’s a sign of a problem within your facility.