Read Me for key understanding (Concept, Target Range, Calculation)

Test for Nutrient Availability - Phosphorus as Orthophosphate

- About this test

This document serves as guidance to test for Phosphorus Availability, as measured as Ortho-Phosphate in the Aeration Basin effluent or outlet end. Essential information is presented in the form of Q&A. In the next page, you will have to enter your measured Ortho-Phosphate in mg/L.

- What are the key nutrients that your bugs require?

- Phosphorus (N)

- Phosphorus (P)

- Iron (Fe)

- Why is Nutrient Availability important for your facility’s performance?

- Like humans, your bugs need critical nutrients to perform functions like digestion, reproduction, etc. In the absence of enough nutrients, their metabolism slows down and the BOD goes untreated.

- In case of a nutrient deficiency, a slime tends to form around the floc which interferes with the settling and causes foaming problems when aerated.

- Among higher life-forms, flagellates especially are susceptible to deficiency in Nitrogen. A large number of flagellates in an advanced stage of the activated sludge process indicates the presence of a large amount of soluble organic nutrients.

- What are measurement units of Nutrient concentrations?

Nutrient concentrations are measured in mg/L or ppm

- What are monitoring locations for Nutrient concentrations?

Aeration Basin outlet end or effluent

- What is an ideal range of Phosphorus Availability?

Aeration Basin effluent, or near the wastewater near the outlet end must contain 1-2 mg/L of Ortho-Phosphate.

- How do you measure or calculate Phosphorus concentration?

A brief summary is given below (Source: EPA). For details, refer to EPA Method 365.3 : Phosphorus, All Forms (Colorimetric, Ascorbic Acid, Two Reagent) or to APHA Standard Methods: 4500-P (Phosphorus)

Monitoring phosphorus involves measuring very low concentrations down to 0.01 mg/L or lower. Even such very low concentrations of phosphorus can have a dramatic impact downstream. Less sensitive methods should be used only to identify serious problem areas.

Orthophosphate is the most common form of phosphorus occurring in wastewater. It is also commonly referred to as “phosphate” and “reactive Phosphorus”. There are three colorimetric methods used to measure Total Orthophosphate to a reasonable degree of accuracy:

- Vanadomolybdo-Phosphoric Acid / ‘Yellow’ Method 
(for routine analysis in range of 1 to 20 mg/L of Ortho-P)

- Ascorbic Acid / ‘Blue’ Method (for range of 0.01 to 6 mg/L of Ortho-P)

- Stannous chloride method (for range of 0.01 to 6 mg/L of Ortho-P)

A reagent (either liquid or powder) containing ascorbic acid and ammonium molybdate reacts with orthophosphate in the sample to form either a blue or yellow compound, depending on the method. The intensity of the blue or yellow color is directly proportional to the amount of orthophosphate in the water.

- Things to keep in mind to ensure accurate measurement of Phosphorus:

- Ensure you account for all flows entering the Aeration Basins

- Ensure your flowmeters are cleaned and calibrated from time to time

- Further corrective actions, if required, will be specified in the Troubleshooting section

- Next step:

In the next page, you will have to input the average of your measured Phosphorus conc. (in mg/L of Ortho-Phosphate) at outlet ends or effluent channels all Aeration Basins in service. Jarvis will use this input to test or check if it’s a sign of a problem within your facility.