## Sheet1
Refer to the table below. Enter a number between 1 and 7 that best matches your observations from the Settleometer Test
Sampling Point | Ideal Observation ID | Recorded Observation ID | Code
Aeration Basin - Outlet end | 1
Result Combinations (BACKEND)
Sampling Point | Result | Condition | Code
D : Aeration Basin - Outlet end | Normal settling sludge, producing clear supernate | 1 | R22.1D
D : Aeration Basin - Outlet end | Rapid settling sludge, without layers, producing cloudy supernate with pin flocs due to very old or over-oxidized sludge condition | 2 | R22.2D
D : Aeration Basin - Outlet end | Rapid settling sludge, after previous normal settling, producing cloudy, dirty, brown supernate - possibly due to deflocculation from toxic upset / excess wasting / turbulence / washout | 3 | R22.3D
D : Aeration Basin - Outlet end | Slow or very slow settling sludge, leaving cloudy or grey-green supernate with stragglers | 4 | R22.4D
D : Aeration Basin - Outlet end | Slow or very slow settling sludge, leaving clear or very clear supernate | 5 | R22.5D
D : Aeration Basin - Outlet end | Rising or floating sludge, producing bubbles on the supernate surface. Popping sound of bubbles. | 6 | R22.6D
D : Aeration Basin - Outlet end | Rising or floating sludge, producing bubbles on the supernate surface. Smell of rotten eggs or cabbages. | 7 | R22.7D
Note down the Observation ID that best matches with what you see. (FRONTEND)
Observation ID | Settling Behavior | Flocs or MLSS | Supernatant
1 | Steady settling (not too fast, not too slow). Sludge compacts, squeezing out water to form different channels. Small particles aggregate to form bigger ones in the first 5 mins. Settled sludge volume after 5 mins is roughly twice that after 30 mins. | Round or Irregular shaped. Dense. Medium-sized. | Clear or Very Clear
2 | Rapid Settling. Sludge drops out, settling in a heap without layering. Settled sludge volume after 5 mins is not much higher than that after 30 mins. | Dense sludge, but individual particles don't aggregate. | Cloudy, with tiny pin flocs
3 | Rapid Settling. Previous settling tests showed sludge settling steadily. Settled sludge volume after 5 mins is not much higher than that after 30 mins. | Dense sludge, but individual particles don't aggregate. | Cloudy, Dirty, Brown
4 | Slow or Very Slow Settling. Poor compaction. Some straggler or dispersed particles may not settle at all. Little to Very Little Settled sludge volume within the first 5 mins. | Light, Fluffy, Not Dense | Cloudy, possibly Gray-Green, with large stragglers or dispersed particles
5 | Slow or Very Slow Settling. Poor compaction. Some straggler or dispersed particles may not settle at all. Little to Very Little Settled sludge volume within the first 5 mins. | Somewhat Light | Clear or Very Clear
6 | Rising / Floating Sludge. Most of the sludge floats to the top within a few hours. | Dense sludge, but individual particles don't aggregate. | Bubbles seen on surface, especially after stirring lightly. Possible pop sound.
7 | Rising / Floating Sludge. Most of the sludge floats to the top within a few hours. | Dense sludge, but individual particles don't aggregate. | Bubbles seen on surface, especially after stirring lightly. Smell of rotten eggs or cabbage.