Read Me for key understanding (Concept, Target Range, Calculation)

Test for SVI - Settleometer Observations

- About this test

This document serves as guidance to test for Sludge Volume Index or SVI, through the Settleometer Test. Essential information is presented in the form of Q&A in the sections below. In the next page, you will have to enter the ID corresponding to entries in the table below that best describe your observations from the test:

| ID | Settling Behavior | Flocs or MLSS | Supernatant (water above sludge) |
| --- | --- | --- | --- |
| 1 | Steady settling (not too fast, not too slow). Sludge compacts, squeezing out water to form different channels. Small particles aggregate to form bigger ones in the first 5 mins. Settled sludge volume after 5 mins is roughly twice that after 30 mins. | Round or Irregular shaped. Dense. Medium-sized. | Clear or Very Clear |
| 2 | Rapid Settling. Sludge drops out, settling in a heap without layering. Settled sludge volume after 5 mins is not much higher than that after 30 mins. | Dense sludge, but individual particles don't aggregate. | Cloudy, with tiny pin flocs |
| 3 | Rapid Settling. Previous settling tests showed sludge settling steadily. Settled sludge volume after 5 mins is not much higher than that after 30 mins. | Dense sludge, but individual particles don't aggregate. | Cloudy, Dirty, Brown |
| 4 | Slow or Very Slow Settling. Poor compaction. Some straggler or dispersed particles may not settle at all. Little to Very Little Settled sludge volume within the first 5 mins. | Light, Fluffy, Not Dense | Cloudy, possibly Gray-Green, with large stragglers or dispersed particles |
| 5 | Slow or Very Slow Settling. Poor compaction. Some straggler or dispersed particles may not settle at all. Little to Very Little Settled sludge volume within the first 5 mins. | Somewhat Light | Clear or Very Clear |
| 6 | Rising / Floating Sludge. Most of the sludge floats to the top within a few hours. | Dense sludge, but individual particles don't aggregate. | Bubbles seen on the surface, especially after stirring lightly. Possible pop sound. |
| 7 | Rising / Floating Sludge. Most of the sludge floats to the top within a few hours. | Dense sludge, but individual particles don't aggregate. | Bubbles seen on the surface, especially after stirring lightly. Smell of rotten eggs or cabbage. |

- What is SVI?

SVI is the Volume (in mL) occupied by 1 gram of sludge that is allowed to settle by gravity, within a settling column or settleometer, after a duration of time (typically, 30 mins). Thus, SVI indicates the relative settleability and compactability of the sludge.

- What is the significance of the Settleometer Test? Why is SVI an important parameter?

Your wastewater treatment facility has to carry out two critical functions :

- Digestion of waste polluting matter (organics) - in Aeration Basins

- Separation of solids (digested matter) and liquids - in Clarifiers

SVI as an index of sludge settleability, indicates the potential for solid-liquid separation. Hence, it is a parameter that needs constant monitoring through the Settleometer Test. A Settleometer is basically a large cylinder of 1 L or 2 L, that allows sludge to settle quietly. It shows how settling would take place within the clarifier.

The Settleometer Test enables close inspection of sludge settling characteristics over a time duration of typically 60 mins. Observations from the test as well as the final SVI value offer insights into underlying problems or changes that affect settleability. This helps operators effect changes to prevent problems.

Since the settleometer models the ideal clarifier, the settled sludge concentration at the bottom of the settleometer models the thickened sludge to be recycled as RAS. The correct RAS concentration is that of the settled sludge. Based on this, the appropriate RAS pumping rate is determined to produce this concentration.

- What are measurement units of SVI?

SVI is an index, hence it is dimensionless. An SVI of 80, for example, means 80 mL of volume for 1 gram of settled sludge.

- What is an ideal range of SVI?

Typically, 80 to 110, but it varies from facility to facility.

Lower SVI values are desirable, as they indicate lower volume occupied by 1 gram of sludge, ie, good compaction (but very low SVI is a sign of an overoxidized or very old sludge). Higher SVI values indicate slower settling, which could be the result of process upsets, excessive solids loading, environmental factors, physical design, etc.

- What are monitoring / sampling locations for the Settleometer Test?
Collect samples from well-mixed wastewater at the Secondary Clarifier Center-Well or Aeration Basin outlet end

- How do you do the Settleometer Test and calculate SVI?

The standard settleometer test involves a fresh wastewater sample being allowed to settle within the settleometer for typically 60 mins. Details of the test are provided further below. SVI is calculated per the equation below at an appropriate settling time interval, typically 30 or 40 mins. It is denoted as SVI30 or SVI40 accordingly. Select

SVI = 
Settled Sludge Volume (mL) x 1000 /

(Volume of Settleometer (L) x MLSS conc. (mg/L))

Guidelines for appropriate settling time selection:

The standard settling time used for calculation is 30 minutes. However, for different sludge settling rates, you can select the appropriate settling time as follows. Precise time selection can be done by developing settling curves, per the procedure described in detail, further below.

Rapid Settling Sludge: 15 to 30 mins

Normal Settling Sludge: 40 to 60 mins

Slow Settling Sludge: 100 to 140 mins

Sample Calculation:
Assuming,
Volume of Settleometer = 2 L

MLSS = 2500 mg/L

Chosen settling time = 30 mins

Settled sludge volume, after 30 mins = 600 mL

SVI30 = 600 x 1000 / (2 x 2500)

SVI30 = 120

- Settleometer Test, in detail:

- Equipment required:

- 2-liter Mallory Settleometer with a wide, plastic stirrer

- Laboratory clock

- Pipette with suction bulb

- Procedure:

- Collect well-mixed wastewater samples near the Aeration Basin Effluent Weirs, or the Secondary Clarifier.

- Pour the sample gently into the settleometer

- Gently mix with a wide paddle and stop any currents in the water.

- Draft the table below. Keep it ready for recording data during sludge settling.

- Start the timer on the laboratory clock, and observe sludge settling.

| I | II | III | IV |
| --- | --- | --- | --- |
| Time (mins) | Settled Sludge Volume (mL) | Observations | Settled Sludge Conc. (mg/L) |
| 0 |  | Record the following at the appropriate time intervals (recommended during the first 5 to 10 mins): A. How does the floc look? Granular / Fluffy / Compact / Feathery B. Describe the floc size Large / Small C. How is the sludge settling? As a blanket / As individual particles D. How does the supernatant (clear water above the sludge) look? Clear / Cloudy E. Do you observe large, fluffy straggler floc? Yes / No |  |
| 5 |  |  |  |
| 10 |  |  |  |
| 15 |  |  |  |
| 20 |  |  |  |
| 25 |  |  |  |
| 30 |  |  |  |
| 40 |  |  |  |
| 50 |  |  |  |
| 60 |  |  |  |
| 90 | Record settled sludge volume for these times, only if the sludge is settling too slowly. |  |  |
| 120 |  |  |  |
| 150 |  |  |  |
| 180 |  |  |  |
| 240 |  |  |  |

- Recording Table Data : Columns II, III, IV

- Col. II : Record the Settled Sludge Volume (mL) next to all the time durations in Col. I, upto 60 mins. If the sludge settles too slowly, continue recording Settled Sludge Volume for time durations 90 mins and beyond. You can stop recording when nearly all of the sludge has settled.

- Col. III : Record observations of flocs and settling behavior at the relevant times, by answering questions stated in Col. III

- Col. IV : Calculate the Settled Sludge Concentration for all times, using the following formula:
Settled Sludge Concentration (mg/L) = 
MLSS (mg/L) x Volume of Settleometer (L) x 1000 / 
Settled Sludge Volume (mL)

Sample values and observations are filled in the table for reference, as follows:

| I | II | III | IV |
| --- | --- | --- | --- |
| Time (mins) | Settled Sludge Volume (mL) | Observations | Settled Sludge Conc. (mg/L) |
| 0 | Settleometer Volume: 2000 | Record the following at the appropriate time intervals (recommended during the first 5 to 10 mins): A. How does the floc look? Granular / Fluffy / Compact / Feathery B. Describe the floc size Large / Small C. How is the sludge settling? As a blanket / As individual particles D. How does the supernatant (clear water above the sludge) look? Clear / Cloudy E. Do you observe large, fluffy straggler floc? Yes / No | = MLSS x Vol. settleometer x 1000 / Settled Sludge Vol. = 2500 x 2 x 1000 / 2000 = 2500 |
| 5 | 1500 |  | = 3333 |
| 10 | 1200 |  | = 4167 |
| 15 | 1000 |  | = 5000 |
| 20 | 850 |  | = 5882 |
| 25 | 700 |  | = 7143 |
| 30 | 600 |  | = 8333 |
| 40 | 580 |  | = 8621 |
| 50 | 570 |  | = 8772 |
| 60 | 565 |  | = 8850 |
| 90 | Record settled sludge volume for these times, only if the sludge is settling too slowly. |  |  |
| 120 |  |  |  |
| 150 |  |  |  |
| 180 |  |  |  |
| 240 |  |  |  |

- Developing Settling Curve & Selecting Appropriate Settling Time :

Now, you’ll have to plot a graph between Settled Sludge Concentration (Col. IV) in the y-axis and Time (Col. I) on the x-axis. For different rates of settling sludge, the curves will appear similar to the following:

Notice, the curves appear to have a ‘knee’ or ‘bend’. The Time (y-axis) corresponding to this knee or bend, denotes the appropriate settling time for your sludge. The corresponding Settled Sludge Concentration (x-axis) is the appropriate RAS concentration for your return sludge.

Example:

The curve developed from the sample table above, is presented below. The knee or bend of the curve is located, and the corresponding Time and Secondary Sludge Concentration are located and recorded accordingly:
Appropriate Settling Time : 30 mins - this will be used for calculating SVI

Appropriate Settled Sludge Conc. : 8333 mg/L - this will be used for calculating RAS rate, to produce RAS conc. of 8333 mg/L (approximation)

- Final Step: SVI calculation

Now that you have identified the Appropriate Settling Time and Settled Sludge Concentration, you can derive the Settled Sludge Volume from the table, or use the following formula:

Settled Sludge Volume (mL) = 
MLSS (mg/L) x Volume of Settleometer (L) x 1000 / 
Settled Sludge Concentration (mg/L)

In our example, the appropriate settling time identified is 30 mins, and settled sludge conc. Is 8333 mg/L, MLSS = 3000 mg/L, Volume of Settleometer = 2 L.

The settled sludge volume is calculated accordingly:

Settled Sludge Volume (mL) = 3000 x 2 x 1000 / 8333 = 600

SVI = 
Settled Sludge Volume (mL) x 1000 /

(Volume of Settleometer (L) x MLSS conc. (mg/L))

SVI = 600 x 1000 / (2 x 2500) = 120

- What are factors that affect SVI?

SVI = 
Settled Sludge Volume (mL) x 1000 /

(Volume of Settleometer (L) x MLSS conc. (mg/L))

- As seen in the formula, SVI is affected by a few factors:
Numerator:

  - Settled Sludge Volume (SSV):

For the same MLSS, higher the SSV, higher the SVI

    - If your bugs are not forming flocs and settling, this will cause the SSV to increase.

    - Also, if you have too many bugs concentrated, ie, if your MLSS is too high, this will cause the SSV to increase as well.

Denominators:

  - MLSS:

For the same SSV, higher the MLSS, lower the SVI

    - You need to have enough MLSS to lower the SVI. If your MLSS is too low, the solids won’t come together to form flocs and settle. They will remain suspended instead.

- Your design should provide for the ideal SVI through constant monitoring and appropriate process controls like sludge wasting to maintain critical parameters like MLSS, SRT, F/M Ratio

- Things to keep in mind to ensure accurate calculation of SVI:

- Ensure your sample is well mixed to represent the entire MLSS

- Do not use tall graduating cylinders for the settleometer test, as the walls can cause friction which affects settling rates, giving false readings.

- 2 L Mallory Settleometer is preferred, but if otherwise, your settleometer should hold at least 1 L.

- Next step:

In the next page, you will have to enter the ID corresponding to entries in the table below that best describe your observations from the test. Jarvis will use this input to check if it’s a sign of a problem within your facility.

| ID | Settling Behavior | Flocs or MLSS | Supernatant (water above sludge) |
| --- | --- | --- | --- |
| 1 | Steady settling (not too fast, not too slow). Sludge compacts, squeezing out water to form different channels. Small particles aggregate to form bigger ones in the first 5 mins. Settled sludge volume after 5 mins is roughly twice that after 30 mins. | Round or Irregular shaped. Dense. Medium-sized. | Clear or Very Clear |
| 2 | Rapid Settling. Sludge drops out, settling in a heap without layering. Settled sludge volume after 5 mins is not much higher than that after 30 mins. | Dense sludge, but individual particles don't aggregate. | Cloudy, with tiny pin flocs |
| 3 | Rapid Settling. Previous settling tests showed sludge settling steadily. Settled sludge volume after 5 mins is not much higher than that after 30 mins. | Dense sludge, but individual particles don't aggregate. | Cloudy, Dirty, Brown |
| 4 | Slow or Very Slow Settling. Poor compaction. Some straggler or dispersed particles may not settle at all. Little to Very Little Settled sludge volume within the first 5 mins. | Light, Fluffy, Not Dense | Cloudy, possibly Gray-Green, with large stragglers or dispersed particles |
| 5 | Slow or Very Slow Settling. Poor compaction. Some straggler or dispersed particles may not settle at all. Little to Very Little Settled sludge volume within the first 5 mins. | Somewhat Light | Clear or Very Clear |
| 6 | Rising / Floating Sludge. Most of the sludge floats to the top within a few hours. | Dense sludge, but individual particles don't aggregate. | Bubbles seen on the surface, especially after stirring lightly. Possible pop sound. |
| 7 | Rising / Floating Sludge. Most of the sludge floats to the top within a few hours. | Dense sludge, but individual particles don't aggregate. | Bubbles seen on the surface, especially after stirring lightly. Smell of rotten eggs or cabbage. |

- Further Reading:

For a detailed understanding of MLSS and MLVSS - concept, monitoring and calculation, refer to the section below.

Notes on MLSS and MLVSS

- What are MLSS and MLVSS?

- MLSS stands for Mixed Liquor Suspended Solids. This is the average TSS of the water or ‘mixed liquor’ (it is called mixed liquor because of the mixing of the Raw Influent, RAS and the bugs in the reactor).

- MLVSS stands for Mixed Liquor Volatile Suspended Solids. This is the volatile component of MLSS, that is made up of living microorganisms, floating in the water. The rest of the MLSS is inert.

- What’s the difference between TSS, MLSS and MLVSS?

- TSS stands for Total Suspended Solids concentration. It measures the amount of solids floating or suspended (not dissolved) in a certain quantity of water. In other words, it measures the concentration of suspended solids that are over 2 microns in size. TSS could include inert solids like sand and clay, or living (volatile) solids like bacteria and other bugs.

- TSS is the general term, while MLSS refers to the TSS within the Aeration Basins present as mixed liquor.

- MLVSS is the volatile component of MLSS, like VSS is the volatile component of TSS.

- What are measurement units of MLSS and MLVSS?

TSS, MLSS and MLVSS are measured in mg/L or ppm (parts per million).

- How do you measure or calculate MLSS and MLVSS?

MLSS determination:

- Digital measurement - TSS sensors or monitors

- Lab Test (Gravimetric Filtration) - Standard Methods 2540 D, APHA

- Decanter Centrifuge

These are explained in further detail below. Choose the method that works for you.

MLVSS determination:
MLVSS can only be determined using the Lab Test mentioned above, which will be explained further. From the MLSS and MLVSS values, you can determine an average MLVSS / MLSS ratio. If the composition of your total solids is generally stable, you can use the average MLVSS / MLSS ratio in your process calculations, instead of having to measure MLVSS each time.

- Methods to determine MLSS and MLVSS:

I. Digital measurement - TSS sensors or monitors (only MLSS)

About this method:

- There are portable, hand-held meters, sensors, monitors and analyzers available in the market for measuring TSS and a host of other polluting parameters.

- Advantages: Accurate, Saves time and money in the long run, considering TSS is a critical parameter you have to keep monitoring regularly.

- Disadvantages: Electronic device might malfunction, probes could lose sensitivity, require calibration, etc.

Procedure:

- Make sure your probes are rinsed and dried before use. Monitor for TSS at a handful of locations in the vicinity. The readings shouldn't fluctuate (change) too much. Your monitoring locations should have :

  - Well-mixed water (the water looks uniform)

  - Steady flow, not violent (turbulent)

  - No accumulation (build-up) of sediments

Precautions / Sources of Error:

- Make sure to test for TSS correctly as described above. The monitoring location must be uniform (homogenous), so it can be representative.

- Keep the probes clean. Rinse and dry them regularly.

- Check the technical manual for guidance on maintenance and calibration.

Final Calculation:

Read from meter.

Report as TSS or MLSS (for Aeration Basins) : ______ mg/L

II. Lab Test (Gravimetric Filtration) - for MLSS and MLVSS
Standard Methods 2540D, APHA ; USGS I-3765-85; EPA Method 160.2

About this method:

- The sample (whole bottle sample or well mixed sub-sample) is filtered, with rinsing, through a pre-weighed glass fiber filter, and the residue on the filter is dried to constant weight at 103-105℃.

- Advantages: Established method, Cheaper

- Disadvantages: More chances of error, Takes more time and effort

Procedure:

- Sampling : Make sure your sampling containers are rinsed, dried and labeled before use. Monitor for TSS at a handful of locations in the vicinity. Your monitoring locations should have :

  - Well-mixed water (the water looks uniform)

  - Steady flow, not violent (turbulent)

  - No accumulation (build-up) of sediments

- Apparatus & Materials required : Sampling containers, Glass-fiber filter, Wide-bore pipet, Graduated cylinder, Forceps, Dessicator, Muffle Furnace or Convection Oven, Vacuum suction flask, Analytical Balance, Distilled or Deionized water

- Method:

- Pre-wash glass fiber filters (nominal 1.5 μm pore size) with deionized water, bake at 103-105°C (or hotter) for at least 1 hour

- Pre-weigh the filter paper using an analytical balance. Record this weight in mg as M0.

- Make the water samples uniform by vigorously mixing well just before sub-sampling (or use the whole bottle if whole bottle sampling is requested)

- Accurately measure the required sample volume (recommended: 25 mL), and transfer to a filtration apparatus containing a pre-weighed filter. Record this volume in liters as V. For eg, if the volume is 25 mL, record V as 0.025 L.

- Rinse filter with 3 volumes of 10 mL deionized water, or as-required to ensure full rinsing of dissolved salts from all portions of the filter paper using the selected apparatus.

- Leave the filter in the muffle furnace or convection oven at 103° - 105°C for 24 hours.

- Remove and cool inside a dessicator for 15 mins.

- Accurately measure the post-weight of the filter. Record this weight in mg as M1.

- Use the following equation to calculate MLSS in mg/L.

MLSS (mg/L) = (M1 - M0) x 1000 / V
where,
M0 = Weight of tared filter, in mg
M1 = Weight of tared filter, with the dried residue, in mg after heating at 103° - 105°C

V = Volume of sample, in Liters

- Now, set the muffle furnace to 550°C for 2 hours and repeat the steps above. The higher temperature evaporates volatile solids, leaving inserts behind. This time, allow the filter papers to cool in the dessicator for 30 mins.

- Accurately measure the post-weight of the filter. Record this weight in mg as M2.

- Use the following equation to calculate MLVSS in mg/L.

MLVSS (mg/L) = (M1 - M2) x 1000 / V
where,
M1 = Weight of tared filter, with the dried residue, in mg, after heating at 103° - 105°C

M2 = Weight of tared filter, with the dried residue, in mg, after heating at 550°C

V = Volume of sample, in Liters

For NPDES or CWA reporting, consult Standard Methods for the Examination of Water and Wastewater, 2540D or USGS I-3765-85 or EPA Method 160.2.

Precautions / Sources of Error:

- Make sure to sample for TSS correctly as described above. The monitoring location must be uniform (homogenous), so it can be representative.

- Make sure your containers and appartus are always cleaned, rinsed with deionized water, and dried before use.

- Sample temperature should be chilled to ≤ 10℃ immediately after sampling and during transit to the laboratory. In the laboratory, samples must be refrigerated at ≤ 6℃. Avoid freezing to prevent sample breakage.

- Choosing the right filter : Filtration must utilize a glass fiber filter with nominal pore size of ~ 1.5 μm, e.g. using filters such as Whatman 934AH, Gelman A/E, Millipore AP40, Ahlstrom 161, Environmental Express Pro Weigh, or equivalent.

- Drying of filters must be conducted at 103 - 105℃.

- Make sure to transfer the effluent sample gently between appartus.

- Make sure your vacuum suction flask is functioning consistently well.

- Identify any sample that yields a residue mass < 2.5 mg or > 200 mg and report the results as an “estimate” because the mass has exceeded the criteria of this analysis.

III. Decanter Centrifuge

About this method:

- Centrifugation is a technique used to separate phases of different densities.

- Advantages: Convenient, Fast, Can be used to analyze a large number of samples.

- Disadvantages: Susceptible to errors as accuracy is affected by sludge compact-ability

Procedure:

- Sampling : Make sure your sampling containers are rinsed, dried and labelled before use. Monitor for MLSS at a handful of locations in the Aeration Basin. Your monitoring locations should have :

  - Well-mixed water (the water looks uniform)

  - Steady flow, not violent (turbulent)

  - No accumulation (build-up) of sediments

- Apparatus & Materials required : Sampling container, Centrifuge tubes, Decanter Centrifuge Rotor, Transfer pipette, Conical flasks, Analytical balance

- Method :

  - Draw 15 mL aliquot from a well-mixed container

  - Centrifuge for ten minutes at 2000 or 4000 rpm

  - Pour off supernatant, separating and drying the retained solids

  - Weigh the solids

Precautions / Sources of Error:

- Make sure to sample for MLSS correctly as described above. The monitoring location must be uniform (homogenous), so it can be representative.

- Make sure your containers and appartus are always cleaned, rinsed with deionized water, and dried before use.

- Sample temperature should be chilled to ≤ 10℃ immediately after sampling and during transit to the laboratory. In the laboratory, samples must be refrigerated at ≤ 6℃. Avoid freezing to prevent sample breakage.

- Use polypropylene centrifuge tubes with a blue screw cap, not white. Never use glass test tubes.

- Screw on the tube tightly. Check cap for cracks or protrusions.

- Do not fill the centrifuge tube beyond 10 mL.

- When loading your samples into the rotor, ensure it's balanced. Tubes of equal weight must be loaded opposite each other. Use water if you don't have another sample to balance the weight.

- Check the technical manual or project guide to know how long the rotor should run, and for guidance on maintenance.

- Don't remove the tubes quickly or shake them violently. Remove the supernatant carefully without disturbing the residue at the bottom.

Final Calculation:

MLSS (mg/L) = 4200 x Centrifuge tube reading (mL)

* Note: The conversion factor (K value) of 4200 is an approximate average. You can determine this more accurately by graphing out different MLSS (mg/L) values determined using the other two methods, and different Centrifuge tube readings (mL) to get the exact correlation.

Report as MLSS : ______ mg/L