Read Me for key understanding (Concept, Target Range, Calculation)

Test for Specific Oxygen Uptake Rate (SOUR)

- About this test

This document serves as guidance to test for Specific Oxygen Uptake Rate (SOUR). Essential information is presented in the form of Q&A in the sections below. In the next page, you will have to enter the calculated average SOUR for Fed sample

- What is the OUR / SOUR test?

The Oxygen Uptake Rate (OUR) or Respiration Rate represents the rate of oxygen consumption for bugs to digest organic waste and reproduce to form new bugs. Thus, the OUR test determines the rate at which oxygen is removed from the MLSS. It is measured in milligrams of oxygen consumed per liter per hour.

The Specific Oxygen Uptake Rate (SOUR) or Respiration Rate goes a step further. It measures oxygen uptake relative to the amount of microorganisms available. It is measured in milligrams of oxygen consumed per hour, per gram of volatile suspended solids (VSS).

- Why is measuring SOUR important? Why not stop with OUR?

Measuring the oxygen uptake rate gives information about the activity-level, age, health of your bugs. It also gives you an idea of the nature of pollutant loading. Thus, SOUR values offer insights into both Food and Microorganism data, which helps assess critical design numbers like F/M Ratio, SRT, etc. Operators can use SOUR data to make operational changes according to the prevailing situation.

Interpreting SOUR data (Conventional Activated Sludge):

| SOUR | Approx. Range (mg O2/ hr / gram MLVSS) | Interpretation | Reason |
| --- | --- | --- | --- |
| Very low | Less than 4 | Toxic Effect | Very low oxygen uptake shows bugs likely killed by possible toxic load |
| Low | 4 to 8 | Hard to digest substrate (food)/ Low or Dilute Loading/ Old Sludge | Bugs don’t use up too much oxygen as they are not digesting fast enough due to low food / hard to break down. Older sludge also doesn’t use much oxygen due to slow growth. |
| Medium | 8 to 20 | Normal condition | Right balance between loading and available microorganisms |
| High | More than 20 | High Loading/ Plant Start-up condition / Young sludge | Excess food availability results in fast oxygen consumption. This also occurs when bugs are young and growth is fast |

It is recommended to measure SOUR beyond OUR, so that oxygen uptake is assessed specifically with regards to your bugs (O2 uptake rate per gram of VSS). This offers a closer evaluation of the activity level of your bugs.

- What are measurement units of SOUR?

mg. O2 / hour / gram of VSS

- What is a normal range of SOUR?

Conventional Activated Sludge: 8 – 20 mg. O2 / hour / gram of VSS

Step Aeration: 8 – 20 mg. O2 / hour / gram of VSS

Extended Aeration: 3 – 12 mg. O2 / hour / gram of VSS

Contact Stabilization: 5 – 15 or 15 – 30 mg. O2 / hour / gram of VSS

- How do you do the simple OUR / SOUR test?

(Source: Maine DEP)

Equipment Needed:

- DO Meter with BOD Bottle probe

- Two 300mL BOD Bottles

- Magnetic stirrer (if BOD Probe does not have a stirrer)

- Sample

- Timer

- Beaker with diameter slightly larger than the BOD Bottle

Procedure:

- Sample location: Aeration Basin effluent (before Secondary Clarifier) or Aeration Basin Influent (RAS + Aeration Basin influent)

- Measure and record DO and temperature of the wastewater sample.

- Collect 3-4 liters of the wastewater sample and transport the sample to the lab immediately. Do not store. The purpose of immediate analysis of the sample is to prevent changes in its composition, since the living bugs will be continuing their functions at a rapid rate.

- Pour some mixed liquor into the beaker so that when the BOD bottle is placed in the beaker, the mixed liquor will come up to the neck of the bottle.

- Thoroughly mix the sample, remove an aliquot and aerate it to get the DO above 5 mg/L. You can do this by filling half Liter of MLSS into a 1 liter bottle and shaking the bottle gently.

- Fill a 300 mL sample bottle until it overflows. Some bubbles will gather at the top. Tilt the BOD bottle to work the bubbles out of the sample.

- Place the BOD bottle in the beaker. Be sure the mixed liquor level in the beaker remains just below the neck of the BOD bottle.

- Place the DO probe in the bottle, making sure not to trap any bubbles. Begin stirring the sample. Allow a short time (30 – 60 seconds) for the temperature and the probe to stabilize.

- Record the DO every minute for 10 minutes, OR until the DO drop becomes consistent OR until the DO drops below 1 mg/L. Make sure that there is at least 1 mg/L difference between the start time and end time of the test.

Note: If the OUR is extremely high, values may have to be read every 30 seconds and the initial DO may have to be increased to 7-8 mg/L. If that does not provide a satisfactory test dilute the sample with BOD dilution water, reaerate the sample and complete the test again. Calculate the appropriate dilution factor to obtain the OUR of the original sample.

OUR calculation:

OUR = (D1 – D2) x 60 / (T2 – T1)

where,

OUR = Oxygen Uptake Rate, in mg O2 / L / hr

D1 = Initial DO concentration, in mg/L

D2 = Final DO concentration, in mg/L

T1 = Start time, in mins

T2 = End time, in mins

SOUR = OUR x 1000 / (MLSS x MLVSS-to-MLSS Ratio)

where,

SOUR = Specific Oxygen Uptake Rate, in mg O2 / hr / gram VSS

OUR = Oxygen Uptake Rate, in mg O2 / L / hr

MLVSS = Mixed Liquor Suspended Solids, in mg/L

Note:

If you do not have the average MLVSS-to-MLSS ratio, you can determine the ratio in the laboratory using a muffle furnace or convection oven. Refer below for more on MLSS, MLVSS.

- Graph the results by plotting DO (in mg/L) on the vertical axis and time (in minutes) on the horizontal axis.

- Graph the line of best fit of the data. The line should be nearly straight. If there is data at the beginning and/or end of the test that are significantly different from the straight line, disregard that data. The straight line represents the actual microorganism activity.

- Pick two points at the beginning and end on the straight line. Determine the slope of the line. (Rise / Run). Check the illustration below.

- OUR = Slope x 60 = 0.2 x 60 = 12 mg/L/hr

- SOUR = OUR x 1000 / MLVSS (say, MLVSS = 2000 mg/L).

SOUR = 12 x 1000 / 2000 = 6 mg O2/ hr/ gVSS

- How can you use SOUR / OUR test to check for Toxicity?

To check for the health of your microorganisms, you’ll have to do the simple OUR / SOUR test on two samples - fed and unfed, at different states of microbial activity. Use return sludge or RAS instead of MLSS. This is done because it is difficult to obtain a truly mixed sample of MLSS, and also to compare between different states of microbial activity for the same microorganisms. as mentioned below :

- Unfed Sample: RAS + Secondary Effluent (unchlorinated)

- Fed Sample: RAS + Primary Effluent (ie, Aeration Basin Influent)

The Unfed Sample resembles the conditions at the outlet end of the Aeration Basin where there is little organic matter left to digest. So, secondary effluent overflow containing very little loading is mixed with the RAS. The oxygen uptake rate from the Unfed sample shows how active the microorganisms are at rest.

The Fed Sample resembles the conditions at the inlet end of the Aeration Basin where the available food is in plenty. So, primary effluent containing high organic loading is mixed with the RAS. The oxygen uptake rate from the unfed sample shows how active the microorganisms are, after feeding.

Comparing the oxygen uptake rates from the two samples will provide the most accurate information of the state of your activated sludge. This will be elaborated further below.

- What is the lab procedure for the OUR / SOUR test for unfed, fed samples?

Monitoring locations for collecting fed and unfed samples:

- Return Sludge (RAS) line: Monitor for RAS

- Secondary Clarifier Weirs: Monitor for Overflow (Unfed Sample)

- Primary Clarifier Weirs: Monitor for Overflow (Fed Sample)

- Aeration Basin: Monitor for MLVSS

- Use the same procedure as the simple OUR / SOUR. Use the diluted RAS samples - fed and unfed, instead of MLSS.

- To determine the proportion of RAS and dilution water, use the formula below:

RAS (mL) = MLSS conc. (mg/L) x 300 / RAS conc.

For example, say,

MLSS conc. = 2400 mg/L

RAS conc. = 9600 mg/L

RAS Qty. to be used (mL) = 2400 x 300 / 9600 = 75 mL

- Make up the remaining quantity upto 300 mL in the BOD bottle accordingly:

Unfed Sample = RAS (75 mL) + Unchlorinated Secondary Effluent (225 mL)

Fed Sample = RAS (75 mL) + Primary Effluent (225 mL)

- Determine the SOUR for the unfed and fed samples, separately.

- Determine the SOUR Fed-to-Unfed ratio as follows. Jarvis will interpret the ratio and check for any problem:

SOUR Fed-to-Unfed ratio = SOUR (Fed) / SOUR (Unfed)

- Things to keep in mind to ensure accurate calculation of SOUR:

- Ensure you obtain well-mixed samples of RAS, from locations where the flow is not turbulent

- Do not delay or store sample after collection. Take immediately for lab analysis.

- Ensure accurate DO measurements by regularly checking the calibration of your DO meters and cleaning the probes and monitoring equipment. Refer your troubleshooting manual for DO meters for specific requirements or procedures.

- Next step:

In the next page, you will have to input the average of your average calculated SOUR for the Fed Sample. Jarvis will use this input to test or check if it’s a sign of a problem within your facility.

- Further Reading:

For a detailed understanding of SOUR - concept, monitoring and calculation, refer to the section below.

Notes on MLSS and MLVSS

- What are MLSS and MLVSS?

- MLSS stands for Mixed Liquor Suspended Solids. This is the average TSS of the water or ‘mixed liquor’ (it is called mixed liquor because of the mixing of the Raw Influent, RAS and the bugs in the reactor).

- MLVSS stands for Mixed Liquor Volatile Suspended Solids. This is the volatile component of MLSS, that is made up of living microorganisms, floating in the water. The rest of the MLSS is inert.

- What’s the difference between TSS, MLSS and MLVSS?

- TSS stands for Total Suspended Solids concentration. It measures the amount of solids floating or suspended (not dissolved) in a certain quantity of water. In other words, it measures the concentration of suspended solids that are over 2 microns in size. TSS could include inert solids like sand and clay, or living (volatile) solids like bacteria and other bugs.

- TSS is the general term, while MLSS refers to the TSS within the Aeration Basins present as mixed liquor.

- MLVSS is the volatile component of MLSS, like VSS is the volatile component of TSS.

- What are measurement units of MLSS and MLVSS?

TSS, MLSS and MLVSS are measured in mg/L or ppm (parts per million).

- How do you measure or calculate MLSS and MLVSS?

MLSS determination:

- Digital measurement - TSS sensors or monitors

- Lab Test (Gravimetric Filtration) - Standard Methods 2540 D, APHA

- Decanter Centrifuge

These are explained in further detail below. Choose the method that works for you.

MLVSS determination:
MLVSS can only be determined using the Lab Test mentioned above, which will be explained further. From the MLSS and MLVSS values, you can determine an average MLVSS / MLSS ratio. If the composition of your total solids is generally stable, you can use the average MLVSS / MLSS ratio in your process calculations, instead of having to measure MLVSS each time.

- Methods to determine MLSS and MLVSS:

I. Digital measurement - TSS sensors or monitors (only MLSS)

About this method:

- There are portable, hand-held meters, sensors, monitors and analyzers available in the market for measuring TSS and a host of other polluting parameters.

- Advantages: Accurate, Saves time and money in the long run, considering TSS is a critical parameter you have to keep monitoring regularly.

- Disadvantages: Electronic device might malfunction, probes could lose sensitivity, require calibration, etc.

Procedure:

- Make sure your probes are rinsed and dried before use. Monitor for TSS at a handful of locations in the vicinity. The readings shouldn't fluctuate (change) too much. Your monitoring locations should have :

  - Well-mixed water (the water looks uniform)

  - Steady flow, not violent (turbulent)

  - No accumulation (build-up) of sediments

Precautions / Sources of Error:

- Make sure to test for TSS correctly as described above. The monitoring location must be uniform (homogenous), so it can be representative.

- Keep the probes clean. Rinse and dry them regularly.

- Check the technical manual for guidance on maintenance and calibration.

Final Calculation:

Read from meter.

Report as TSS or MLSS (for Aeration Basins) : ______ mg/L

II. Lab Test (Gravimetric Filtration) - for MLSS and MLVSS
	Standard Methods 2540D, APHA ; USGS I-3765-85; EPA Method 160.2

About this method:

- The sample (whole bottle sample or well mixed sub-sample) is filtered, with rinsing, through a pre-weighed glass fiber filter, and the residue on the filter is dried to constant weight at 103-105℃.

- Advantages: Established method, Cheaper

- Disadvantages: More chances of error, Takes more time and effort

Procedure:

- Sampling : Make sure your sampling containers are rinsed, dried and labeled before use. Monitor for TSS at a handful of locations in the vicinity. Your monitoring locations should have :

  - Well-mixed water (the water looks uniform)

  - Steady flow, not violent (turbulent)

  - No accumulation (build-up) of sediments

- Apparatus & Materials required : Sampling containers, Glass-fiber filter, Wide-bore pipet, Graduated cylinder, Forceps, Dessicator, Muffle Furnace or Convection Oven, Vacuum suction flask, Analytical Balance, Distilled or Deionized water

- Method:

- Pre-wash glass fiber filters (nominal 1.5 μm pore size) with deionized water, bake at 103-105°C (or hotter) for at least 1 hour

- Pre-weigh the filter paper using an analytical balance. Record this weight in mg as M0.

- Make the water samples uniform by vigorously mixing well just before sub-sampling (or use the whole bottle if whole bottle sampling is requested)

- Accurately measure the required sample volume (recommended: 25 mL), and transfer to a filtration apparatus containing a pre-weighed filter. Record this volume in liters as V. For eg, if the volume is 25 mL, record V as 0.025 L.

- Rinse filter with 3 volumes of 10 mL deionized water, or as-required to ensure full rinsing of dissolved salts from all portions of the filter paper using the selected apparatus.

- Leave the filter in the muffle furnace or convection oven at 103° - 105°C for 24 hours.

- Remove and cool inside a dessicator for 15 mins.

- Accurately measure the post-weight of the filter. Record this weight in mg as M1.

- Use the following equation to calculate MLSS in mg/L.

MLSS (mg/L) = (M1 - M0) x 1000 / V
where,
M0 = Weight of tared filter, in mg
M1 = Weight of tared filter, with the dried residue, in mg after heating at 103° - 105°C

V = Volume of sample, in Liters

- Now, set the muffle furnace to 550°C for 2 hours and repeat the steps above. The higher temperature evaporates volatile solids, leaving inserts behind. This time, allow the filter papers to cool in the dessicator for 30 mins.

- Accurately measure the post-weight of the filter. Record this weight in mg as M2.

- Use the following equation to calculate MLVSS in mg/L.

MLVSS (mg/L) = (M1 - M2) x 1000 / V
where,
M1 = Weight of tared filter, with the dried residue, in mg, after heating at 103° - 105°C

M2 = Weight of tared filter, with the dried residue, in mg, after heating at 550°C

V = Volume of sample, in Liters

For NPDES or CWA reporting, consult Standard Methods for the Examination of Water and Wastewater, 2540D or USGS I-3765-85 or EPA Method 160.2.

Precautions / Sources of Error:

- Make sure to sample for TSS correctly as described above. The monitoring location must be uniform (homogenous), so it can be representative.

- Make sure your containers and appartus are always cleaned, rinsed with deionized water, and dried before use.

- Sample temperature should be chilled to ≤ 10℃ immediately after sampling and during transit to the laboratory. In the laboratory, samples must be refrigerated at ≤ 6℃. Avoid freezing to prevent sample breakage.

- Choosing the right filter : Filtration must utilize a glass fiber filter with nominal pore size of ~ 1.5 μm, e.g. using filters such as Whatman 934AH, Gelman A/E, Millipore AP40, Ahlstrom 161, Environmental Express Pro Weigh, or equivalent.

- Drying of filters must be conducted at 103 - 105℃.

- Make sure to transfer the effluent sample gently between appartus.

- Make sure your vacuum suction flask is functioning consistently well.

- Identify any sample that yields a residue mass < 2.5 mg or > 200 mg and report the results as an “estimate” because the mass has exceeded the criteria of this analysis.

III. Decanter Centrifuge

About this method:

- Centrifugation is a technique used to separate phases of different densities.

- Advantages: Convenient, Fast, Can be used to analyze a large number of samples.

- Disadvantages: Susceptible to errors as accuracy is affected by sludge compact-ability

Procedure:

- Sampling : Make sure your sampling containers are rinsed, dried and labelled before use. Monitor for MLSS at a handful of locations in the Aeration Basin. Your monitoring locations should have :

  - Well-mixed water (the water looks uniform)

  - Steady flow, not violent (turbulent)

  - No accumulation (build-up) of sediments

- Apparatus & Materials required : Sampling container, Centrifuge tubes, Decanter Centrifuge Rotor, Transfer pipette, Conical flasks, Analytical balance

- Method :

  - Draw 15 mL aliquot from a well-mixed container

  - Centrifuge for ten minutes at 2000 or 4000 rpm

  - Pour off supernatant, separating and drying the retained solids

  - Weigh the solids

Precautions / Sources of Error:

- Make sure to sample for MLSS correctly as described above. The monitoring location must be uniform (homogenous), so it can be representative.

- Make sure your containers and appartus are always cleaned, rinsed with deionized water, and dried before use.

- Sample temperature should be chilled to ≤ 10℃ immediately after sampling and during transit to the laboratory. In the laboratory, samples must be refrigerated at ≤ 6℃. Avoid freezing to prevent sample breakage.

- Use polypropylene centrifuge tubes with a blue screw cap, not white. Never use glass test tubes.

- Screw on the tube tightly. Check cap for cracks or protrusions.

- Do not fill the centrifuge tube beyond 10 mL.

- When loading your samples into the rotor, ensure it's balanced. Tubes of equal weight must be loaded opposite each other. Use water if you don't have another sample to balance the weight.

- Check the technical manual or project guide to know how long the rotor should run, and for guidance on maintenance.

- Don't remove the tubes quickly or shake them violently. Remove the supernatant carefully without disturbing the residue at the bottom.

Final Calculation:

MLSS (mg/L) = 4200 x Centrifuge tube reading (mL)

* Note: The conversion factor (K value) of 4200 is an approximate average. You can determine this more accurately by graphing out different MLSS (mg/L) values determined using the other two methods, and different Centrifuge tube readings (mL) to get the exact correlation.

Report as MLSS : ______ mg/L