Read Me for key understanding (Concept, Target Range, Calculation)

Sludge Blanket Measurements - Core Sampler

- About this test or check

This document serves as guidance towards sludge blanket measurements using the core sampler or sludge judge. Essential information is presented in the form of Q&A in the sections below. In the next page, you will have to enter the measured average Sludge Blanket Depth

- What is a Sludge Blanket?

A Sludge Blanket is a mass of solids that gets built up and maintained to a range of depth in the Secondary Clarifier.

- Why is it necessary to measure Sludge Blanket Thickness?

- Sludge Blanket Thickness is directly related to the return sludge (RAS) concentration. Low RAS flow causes a rising or thick sludge blanket, and higher RAS concentration. High RAS flow causes a falling or thin sludge blanket, and lower RAS concentration.

- Secondary Clarifiers provide additional capacity to store solids. Maintaining a blanket in the clarifiers offers a way to balance your solids inventory, by taking away solids from the Aeration Basin when needed, in the right amounts.

- Process calculations, for eg., SRT or Sludge Age, must take into account solids inventory in the clarifier sludge blanket, if a sludge blanket is maintained.

- What are measurement units of Sludge Blanket Thickness?

feet

- What is an ideal range of Sludge Blanket Thickness?

1 to 3 feet or less than 25% of the Secondary Clarifier depth

- How do you measure Sludge Blanket Depth or Thickness?

You can use Sludge Depth / Blanket Meters or Sensors, to measure the depth of sludge, ie, the distance from the top of the sludge to the clarifier bottom. You can also use a core sampler or sludge judge to measure sludge thickness directly as follows:

- A sludge judge is a core sampler that may consist of 3 to 5 ft. long sections of plastic tubing, each marked at 1 foot intervals for easy measurement.

- The bottom section of the core sampler is fitted with a check valve, which opens as the unit is lowered into the liquid.

- Use the sludge judge to obtain a sample of sludge, over the center well. As you lower the sludge judge, the unit reaches the bottom of the clarifier and the water levels off at the surface. At this point, tug on the retraining rope on the top section. This will set the check valve and retain the sample in the tubing.

- When the unit has been raised clear of the liquid, the amount of solids in the sample can be read using the one foot increments marked on the pipe sections

- To release the material, touch the pin extending from the bottom section against a hard surface. This opens the check valve to drain the sample.

- How do you calculate Sludge Blanket Thickness?

Sludge Blanket Thickness =  Clarifier Sidewater Depth - Depth of Sludge Blanket

OR

Sludge Blanket Thickness =  Read from Sludge Judge

Monitoring locations for determining Sludge Blanket Thickness:

- Secondary Clarifier Center-Well

Sample Calculation:
Avg. sidewater depth of Secondary Clarifier: 14 ft.

Avg. depth of sludge blanket = 11 ft.

Sludge Blanket Thickness = 14 - 11 = 3 ft.

- Things to keep in mind for accurate sampling and measurement:

If there are too many solids in the bed there may be inconsistencies in the bed measurement. It also makes it hard for a consistent return sludge (RAS) to be drawn off the bottoms. Do the following to prevent this from happening.

- Ensure your return sludge (RAS) flow does not fall below a threshold rate.

- Perform regular cleaning and inspection of sludge draw off lines, sludge removal mechanism and secondary clarifiers.

- Next step:

In the next page, you will have to input the average of your measured Sludge Blanket Thickness for all Secondary Clarifiers in service. Jarvis will use this input to test or check if it’s a sign of a problem within your facility.