Read Me for key understanding (Concept, Target Range, Calculation)

Hydraulic Retention Time (HRT) - Primary Clarifiers

- About this test

This document serves as guidance to determine the HRT in your Equalization Basins. Essential information is presented in the form of Q&A in the sections below. In the next page, you will have to enter the average HRT for all Primary Clarifiers in service.

- What is HRT?

Hydraulic Retention Time (HRT) is the average time spent by a water molecule, from entry to exit, within a unit.

- Why is HRT an important parameter?

- HRT is basically the time (in hours or days) you allow for the particular unit to perform its physical / chemical / biological function on the wastewater, from the time it enters to its exit. The HRT has to be sufficient enough to ensure your treatment unit’s performance efficiency.

- So, too short HRT can result in reduced treatment effectiveness, while too long HRT can create anaerobic conditions, causing your wastewater to become septic.

- The idea is to provide just enough HRT, so you can keep the flow going and maximize the influent flow you receive.

- How do you calculate HRT?

Refer to the formula and sample calculation below.

HRT (hours) = Volume of unit (million gal) x 24 / Influent flow rate (MGD)

Influent flow rate = 1.8 MGD (signifies total flow entering Primary Clarifier)
	Volume of Primary Clarifier = 300,000 gal or 0.3 million gal

HRT (hours) = 0.3 x 24 / 1.8

HRT (hours) = 4

- What are the factors that affect HRT?

HRT (hours) = Volume of unit (million gal) x 24 / Influent flow rate (MGD)

- As seen in the formula, the HRT is affected by the size (volume) of the treatment unit and the speed (rate) of flow.

- For a fixed rate of flow entering a treatment unit, if you increase the size (capacity or volume) of the unit, the HRT increases. Decreasing the capacity decreases the HRT.

- For a fixed treatment capacity, if you slow down the flow, the HRT increases. Speeding up the flow decreases the HRT.

- Your design should provide for the ideal HRT by striking a balance between maximum capacity utilization and maximum influent rate of flow.

- What is the role of Primary Clarifiers? How do you ensure their maximum performance?

- Your primary clarifiers play a critical role in removing half of the solids that are usually heavy, settleable. This doesn’t just help with your final discharge norms, it also filters heavy material that can hinder the functioning of your bugs in downstream secondary treatment, enabling them to work specifically on the lighter volatile organics.

- To slow down the flow for effective settling, Clarifiers have EDI’s or Energy Dissipating Inlets which dissipate the kinetic or moving energy of the flow.

- Clarifiers may also have flocculation Center-Wells to help aid the solids settling and reduce the retention time, thus handling larger flows. You’ll want to keep the chemical addition to as minimal as possible to reduce costs and avoid creating too much chemical sludge.

- More on Primary Clarifiers and action steps for their effective O&M will be specified in the Troubleshooting section.

- What is the ideal HRT for Primary Clarifiers?
2 to 4 hours

- What do you need to keep in mind to ensure you calculate HRT accurately for your Primary Clarifiers?

- Ensure you account for all flows entering the Primary Clarifier

- Ensure your flowmeters are cleaned and calibrated from time to time

- Further corrective actions, if required, will be specified in the Troubleshooting section

- Next step:

In the next page, you will have to input the average of your calculated HRT for all Primary Clarifiers in service. Jarvis will use this input to test or check if it’s a sign of a problem within your facility.