## Sheet1
Refer to the table below. Enter a number between 1 and 9 that best matches your observations from the Microscopic evaluation.
Sampling Point | Ideal Observation ID | Recorded Observation ID | Code
Aeration Basin - Outlet End | 9
Result Combinations (BACKEND)
Sampling Point | Result | Condition | Code
D : Aeration Basin - Outlet End | Low DO: Any combination of : S. natans / Type 1701 / H. hydrossis | Input = 1 | R31.1D
D : Aeration Basin - Outlet End | Low F/M ratio: Any combination of : N. limicola I, II, III / H. hydrossis / Type 0041 / Type 0675 / Type 1851 / Type 0092 / Type 0803 / Type 0581 / Type 0211 | Input = 2 | R31.2D
D : Aeration Basin - Outlet End | Excess Organic Acids: Any combination of : Zooglea / Beggiatoa / N. limicola I, II, III / Thiothrix I, II / Type 021N / Type 0092 / Type 0581 / Type 0914 / Type 0803 / Type 0411 / Type 0961 / Type 0211 | Input = 3 | R31.3D
D : Aeration Basin - Outlet End | Septicity: Any combination of : Beggiatoa / N. limicola I, II, III / Thiothrix I, II / Zooglea / Type 021N / Type 0914 / Type 0803 / Type 0092 / Type 0581 / Type 0411 / Type 0961 / Type 0211 | Input = 4 | R31.4D
D : Aeration Basin - Outlet End | Nutrient Deficiency: Any combination of : H. hydrossis / N. limicola I, II, III / Beggiatoa / S. natans / Thiothrix I, II / Zooglea / Fungi / Type 0041 / Type 0675 / Type 021N / Type 0914 | Input = 5 | R31.5D
D : Aeration Basin - Outlet End | Low pH: Fungi | Input = 6 | R31.6D
D : Aeration Basin - Outlet End | Foaming: Any combination of M. parvicella, Nocardia, Type 1863 | Input = 7 | R31.7D
D : Aeration Basin - Outlet End | No Filaments: No or very few filaments seen, flocs appear dispersed. | Input = 8 | R31.8D
D : Aeration Basin - Outlet End | Normal: No dominance of any of the above. Good mix of flocs & filaments. | Input = 9 | R31.9D
Note down the Observation ID that best matches with what you see. (FRONTEND)
Observation ID | Microscopic Observation
1 | Low DO: Any combination of : S. natans / Type 1701 / H. hydrossis
2 | Low F/M ratio: Any combination of : N. limicola I, II, III / H. hydrossis / Type 0041 / Type 0675 / Type 1851 / Type 0092 / Type 0803 / Type 0581 / Type 0211
3 | Excess Organic Acids: Any combination of : Zooglea / Beggiatoa / N. limicola I, II, III / Thiothrix I, II / Type 021N / Type 0092 / Type 0581 / Type 0914 / Type 0803 / Type 0411 / Type 0961 / Type 0211
4 | Septicity: Any combination of : Beggiatoa / N. limicola I, II, III / Thiothrix I, II / Zooglea / Type 021N / Type 0914 / Type 0803 / Type 0092 / Type 0581 / Type 0411 / Type 0961 / Type 0211
5 | Nutrient Deficiency: Any combination of : H. hydrossis / N. limicola I, II, III / Beggiatoa / S. natans / Thiothrix I, II / Zooglea / Fungi / Type 0041 / Type 0675 / Type 021N / Type 0914
6 | Low pH: Fungi
7 | Foaming: Any combination of M. parvicella, Nocardia, Type 1863
8 | No Filaments: No or very few filaments seen, flocs appear dispersed.
9 | Normal: No dominance of any of the above. Good mix of flocs & filaments.

## Sheet2
Beggiatoa | Nitrogen DEF ¦ Sulfide/Septicity ¦ Excess Organic Acids - Septage, INF Changes ¦ Pipes/attached growth systems, slough off, cause FIL grwth ¦ Organic Overload ¦ High F:M
Fungi
H. hydrossis
M. parvicella
Nocardia
N. limicola I
N. limicola II
N. limicola III
S. natans | Low DO
Thiothrix I
Thiothrix II
Zooglea (Zoogloea ramigera)
Type 0041
Type 0092
Type 021N
Type 0411
Type 0581
Type 0675
Type 0803
Type 0914
Type 0961
Type 1701
Type 1851
Type 1863