Read Me for key understanding (Concept, Target Range, Calculation)

Surface Overflow Rate (SOR) - Secondary Clarifiers

- About this test

This document serves as guidance to determine the Surface Overflow Rate (SOR) for Secondary Clarifiers. Essential information is presented in the form of Q&A in the sections below. In the next page, you will have to enter the average SOR for all Secondary Clarifiers in service.

- What is SOR?

Surface Overflow Rate (SOR) is the rate of overflow through the clarifier per unit surface area of the clarifier, that is, the number of gallons per day (GPD) flowing over 1 sq.ft. of your clarifier’s surface. This is indicative of the potential for high velocities of secondary effluent flow. This tells you whether you’re allowing enough time for your solids to settle in the clarifier. SOR is measured in GPD per square foot, ie, gal / day / sq.ft.

- Why is SOR an important parameter?

- Your primary and secondary clarifiers must be able to hold the water for long enough to allow solids to settle down. For this to happen, the rate or speed of your overflow has to be equal to or less than that of solids settling. This depends on the amount of solids loading into your clarifiers relative to their capacity, and how smoothly flows are introduced without creating turbulence.

- So, if your SOR is too high, your solids will wash out over the weirs, causing an increase in the effluent TSS. But if your SOR is too low, this would mean you’re retaining solids for too long in the clarifier, which can create anaerobic conditions, causing your wastewater to become septic. A lower than ideal SOR also means you are taking in too little flow relative to the surface area of your clarifiers, which is not cost effective.

- The idea is to provide just enough SOR, so you can allow solids enough time to settle, while keeping the flow going and maximizing the influent flow you receive.

- How do you calculate SOR?

Refer to the formula and sample calculation below.

SOR (GPD / sq.ft) = Secondary Effluent flow (million gal) x 106 / Area of clarifier (sq. ft)

Step (i) : Calculating total flow leaving Secondary Clarifier through weirs
You can determine the flow through a flow meter, or derive it from known flows demonstrated below.

Total flow = FRaw + (FFil . 10-6) – FD – (FWASp . TWASp . 24 . 10-6)  – (FWASs . TWASs . 24 . 10-6)

where,

Total flow : Total secondary effluent flow through weirs (MGD)
	FRaw : Total raw influent flow received by your facility (MGD)

FFil : Filtrate from Sludge thickening, dewatering (GPD or gal per day)

FD : Diverted Sidestream flow bypassing Secondary Treatment (MGD)

FWASp : Primary WAS Flow (GPM or gal per min)

FWASs : Secondary WAS Flow (GPM or gal per min)

TWASp : Minutes of operation of Primary WAS pump per hour, on average

TWASs : Minutes of operation of Secondary WAS pump per hour, on average

Example:
	Raw influent flow (FRaw) = 1.2 MGD

Filtrate from Sludge thickening, dewatering (FFil) = 50,000 GPD

Diverted Sidestream flow bypassing Secondary Treatment (FD) = 0.2 MGD
	Primary WAS Flow (FWASp) = 80 GPM

Secondary WAS Flow (FWASs) = 90 GPM

Minutes of operation of Primary WAS pump per hour (TWASp) = 25

Minutes of operation of Secondary WAS pump per hour (TWASs) = 15

Total Secondary Effluent Flow through Weirs (MGD) 
	= 1.2 + (50,000 . 10-6) – 0.2 – (80 . 25 . 24 . 10-6)  – (90 . 15 . 24 . 10-6)

= 0.97 MGD

Note - if you don’t run your WAS pumps every hour, follow the calculation below:

TWAS (mins / hr) = Total hours of operation per day x 60 / 24

Total hours of operation per day : 8
	TWAS = 8 x 60 / 24 = 20 mins / hr

Step (ii) : Calculating SOR
SOR (GPD / sq.ft) = Secondary Effluent flow (million gal) x 106 / Area of clarifier (sq. ft)

Secondary Effluent Flow : 0.97 MGD

Surface Area of Clarifier : 1200 sq.ft 
	SOR = 0.97 x 106 / 1200

SOR = 808 GPD / sq.ft

Note - To determine the Surface Area of your Clarifier, follow the calculation below:
	
	For circular clarifiers:

Surface Area (sq.ft) = (22/7) x (1/4) x (Diameter)^2

Diameter : 30 ft.

Surface Area = (22/7) x (1/4) x (30)^2 = 707 sq.ft

For rectangular clarifiers:

Surface Area (sq.ft) = Length x Width

Length : 30 ft.

Width : 25 ft.

Surface Area = 30 x 25 = 750 sq.ft

- What are the factors that affect SOR?

SOR (GPD / sq.ft) = Secondary Effluent flow (million gal) x 106 / Area of clarifier (sq. ft)

- As seen in the formula, the SOR is affected by the spatial extent (surface area) of the treatment unit and the speed (rate) of flow entering the secondary clarifier.

- For a fixed rate of flow entering the clarifier, if you increase the spatial extent (surface area) of the secondary clarifier, the SOR decreases. Decreasing the surface area increases the SOR.

- For a fixed surface area, if you slow down the flow, the SOR decreases. Speeding up the flow increases the SOR.

- Your design should provide for the ideal SOR by striking a balance between maximum surface area utilization and maximum influent rate of flow.

- What is the ideal SOR?
600 to 1200 GPD / sq.ft

- What do you need to keep in mind to ensure you calculate SOR accurately?

- Ensure you account for all flows entering the Secondary Clarifier, as demonstrated in the calculation steps

- Ensure your flowmeters are cleaned and calibrated from time to time

- Further corrective actions for secondary clarifiers, if required, will be specified in the Troubleshooting section

- Next step:

In the next page, you will have to input the average of your calculated SOR for all Secondary Clarifiers in service. Jarvis will use this input to test or check if it’s a sign of a problem within your facility.