Read Me for key understanding (Concept, Target Range, Calculation)

Weir Overflow Rate (WOR) - Secondary Clarifiers

- About this test

This document serves as guidance to determine the Weir Overflow Rate (WOR) for Secondary Clarifiers. Essential information is presented in the form of Q&A in the sections below. In the next page, you will have to enter the average WOR for all Secondary Clarifiers in service.

- What is WOR?

Weir Overflow Rate (WOR) is similar to Surface Overflow Rate (SOR), except that the Weir length is considered instead of the Surface Area of the clarifier.

WOR is the rate of overflow through the clarifier weirs per unit length of the weirs, that is, the number of gallons per day (GPD) flowing over 1 ft. of your clarifier’s weirs. This is indicative of the potential for high velocities of secondary effluent flow through your weirs. This tells you whether you’re allowing enough time for your solids to settle in the clarifier. WOR is measured in GPD per linear foot, ie, gal / day / lin.ft

- Why is WOR an important parameter?

- Your primary and secondary clarifiers must be able to hold the water for long enough to allow solids to settle down. For this to happen, the rate or speed of your overflow has to be equal to or less than that of solids settling. This depends on the amount of solids loading into your clarifiers relative to their capacity, and how smoothly flows are introduced without creating turbulence.

- So, if your WOR is too high, your solids will wash out over the weirs, causing an increase in the effluent TSS. But if your WOR is too low, this would mean you’re retaining solids for too long in the clarifier, which can create anaerobic conditions, causing your wastewater to become septic. A lower than ideal WOR also means you are taking in too little flow relative to the surface area of your clarifiers, which is not cost effective.

- The idea is to provide just enough WOR, so you can allow solids enough time to settle, while keeping the flow going and maximizing the influent flow you receive.

- How do you calculate WOR?

Refer to the formula and sample calculation below.

WOR (GPD / lin.ft) = Secondary Effluent flow (million gal) x 106 / Total Length of Clarifier Weirs (sq. ft)

Step (i) : Calculating total flow leaving Secondary Clarifier through weirs
You can determine the flow through a flow meter, or derive it from known flows demonstrated below.

Total flow = FRaw + (FFil . 10-6) – FD – (FWASp . TWASp . 24 . 10-6)  – (FWASs . TWASs . 24 . 10-6)

where,

Total flow : Total secondary effluent flow through weirs (MGD)
	FRaw : Total raw influent flow received by your facility (MGD)

FFil : Filtrate from Sludge thickening, dewatering (GPD or gal per day)

FD : Diverted Sidestream flow bypassing Secondary Treatment (MGD)

FWASp : Primary WAS Flow (GPM or gal per min)

FWASs : Secondary WAS Flow (GPM or gal per min)

TWASp : Minutes of operation of Primary WAS pump per hour, on average

TWASs : Minutes of operation of Secondary WAS pump per hour, on average

Example:
	Raw influent flow (FRaw) = 1.2 MGD

Filtrate from Sludge thickening, dewatering (FFil) = 50,000 GPD

Diverted Sidestream flow bypassing Secondary Treatment (FD) = 0.2 MGD
	Primary WAS Flow (FWASp) = 80 GPM

Secondary WAS Flow (FWASs) = 90 GPM

Minutes of operation of Primary WAS pump per hour (TWASp) = 25

Minutes of operation of Secondary WAS pump per hour (TWASs) = 15

Total Secondary Effluent Flow through Weirs (MGD) 
	= 1.2 + (50,000 . 10-6) – 0.2 – (80 . 25 . 24 . 10-6)  – (90 . 15 . 24 . 10-6)

= 0.97 MGD

Note - if you don’t run your WAS pumps every hour, follow the calculation below:

TWAS (mins / hr) = Total hours of operation per day x 60 / 24

Total hours of operation per day : 8
	TWAS = 8 x 60 / 24 = 20 mins / hr

Step (ii) : Calculating WOR
WOR (GPD / lin.ft) = Secondary effluent flow (million gal) x 106 / Total length of clarifier weirs (lin. ft)

Secondary Effluent Flow : 0.97 MGD

Total Length of Clarifier Weirs : 100 lin.ft 
	WOR = 0.97 x 106 / 100

WOR = 9,700 GPD / lin.ft

Note - If you do not know the total weir length, you can derive it by using the calculation below. The total weir length is basically the circumference or perimeter of the clarifier.

Total Weir Length (lin.ft) = (22/7) x Weir Diameter

Weir Diameter : 30 ft.

Total Weir Length = (22/7) x 30 = 94 lin.ft

- What are the factors that affect WOR?

WOR (GPD / lin.ft) = Secondary effluent flow (million gal) x 106 / Total length of clarifier weirs (lin.ft)

- As seen in the formula, the WOR is affected by the spatial extent or total length of the clarifier weirs, and the speed (rate) of flow entering the secondary clarifier. The total weir length represents the circumference or perimeter of the clarifier.

- For a fixed rate of flow entering the clarifier, if you increase the spatial extent (total weir length) of the clarifier, the WOR decreases. Decreasing the total weir length increases the WOR.

- For a fixed total weir length, if you slow down the flow, the WOR decreases. Speeding up the flow increases the WOR.

- Your design should provide for the ideal WOR by striking a balance between maximum total weir length utilization and maximum influent rate of flow.

- What is the ideal WOR?
10,000 to 15,000 GPD / lin.ft (ideal), nothing over 20,000 GPD / lin.ft

- What do you need to keep in mind to ensure you calculate WOR accurately?

- Ensure you account for all flows entering the Secondary Clarifier, as demonstrated in the calculation steps

- Ensure your flowmeters are cleaned and calibrated from time to time

- Further corrective actions for secondary clarifiers, if required, will be specified in the Troubleshooting section

- Next step:

In the next page, you will have to input the average of your calculated WOR for all Secondary Clarifiers in service. Jarvis will use this input to test or check if it’s a sign of a problem within your facility.