Read Me for key understanding (Concept, Target Range, Calculation)

Organic Loading Rate (OLR) - Aeration Basins

- About this test

This document serves as guidance to determine the Organic Loading Rate (OLR) for Aeration Basins. Essential information is presented in the form of Q&A in the sections below. In the next page, you will have to enter the average OLR for all Aeration Basins in service.

- What is OLR?

Organic Loading Rate (OLR) is the rate of food or organics (BOD) received by your Aeration Basins per unit volume of surface area. It represents the rate of pollutant loading to your secondary treatment stage.

- Why is OLR an important parameter?

OLR is the starting design number that decides the size or extent of secondary treatment required. The extent of incoming organics determines how many bugs you need, ie, the MLVSS concentration you require to provide the ideal F/M Ratio (Food to Microorganism Ratio) or SRT (Solids Retention Time)

- What are measurement units of SLR?

OLR is measured in units of lbs/day / 1000 gal (Volumetric OLR).

- What is an ideal range of OLR?

4 to 8 lbs/day for every 1000 gal of aeration capacity

- How do you calculate OLR?

OLR (lbs/day / 1000 gal) 
= BOD (lbs/day) / (Volume of Aeration Basin (million gal) x 1000)

=>

OLR (lbs/day / 1000 gal) =

Total Flow entering Aeration Basins (MGD) x Influent BOD conc. (mg/L) x 8.34 / (Volume of Aeration Basin (million gal) x 1000)

Monitoring locations for determining SLR:

- Aeration Basin : Monitoring for influent flow, influent BOD concentration

Sample Calculation:
Total Flow entering Aeration Basin : 1.3 MGD

Influent BOD conc. : 250 mg/L

Volume of Aeration Basin : 0.75 million gal

OLR = 1.3 x 250 x 8.34 / (0.75 x 1000)

OLR = 3.6 lbs / day / 1000 gal

A detailed calculation is provided further below.

- What are factors that affect OLR?

OLR (lbs/day / 1000 gal) =

Total Flow entering Aeration Basins (MGD) x Influent BOD conc. (mg/L) x 8.34 / (Volume of Aeration Basin (million gal) x 1000)

- As seen in the formula, the OLR is affected by three factors:

Numerators:

  - Influent flow => Higher flow, means higher OLR and vice versa

  - Influent BOD conc. => Higher BOD, means higher OLR and vice versa

Denominator:

  - Volume of Aeration Basins => Higher Volume, means lower OLR and vice versa

- Your design should provide for the ideal OLR by sizing the appropriate capacity for the expected BOD concentration and influent flow received.

- The extent of pollutant loading may require changes in process configuration. For example, Modified aeration or Contact stabilization modes are suitable for higher organic loads (OLR)

- Things to keep in mind to ensure accurate calculation of OLR:

- Ensure you account for all flows entering the Aeration Basins

- Ensure your flowmeters are cleaned and calibrated from time to time

- Further corrective actions, if required, will be specified in the Troubleshooting section

- Next step:

In the next page, you will have to input the average of your calculated OLR for all Aeration Basins in service. Jarvis will use this input to test or check if it’s a sign of a problem within your facility.

- Detailed Calculation:

OLR (lbs/day / 1000 gal) 
= BOD (lbs/day) / (Volume of Aeration Basin (million gal) x 1000)

Step (i) : Calculating total flow entering Aeration Basins
You can determine the influent flow through a flow meter, or derive it from known flows demonstrated below.

Total flow = FRaw + (FFil . 10-6) – FD – (FWASp . TWASp . 24 . 10-6) + FRAS

where,

Total flow : Total flow entering Aeration Basins (MGD)
	FRaw : Total raw influent flow received by your facility (MGD)

FFil : Filtrate from Sludge thickening, dewatering (GPD or gal per day)

FD : Diverted Sidestream flow bypassing Secondary Treatment (MGD)

FWASp : Primary WAS Flow (GPM or gal per min)

FRAS : RAS Flow (MGD)

TWASp : Minutes of operation of Primary WAS pump per hour, on average

Example:
	Raw influent flow (FRaw) = 1.2 MGD

Filtrate from Sludge thickening, dewatering (FFil) = 50,000 GPD

Diverted Sidestream flow bypassing Secondary Treatment (FD) = 0.2 MGD
	Primary WAS Flow (FWASp) = 80 GPM

RAS Flow (FRAS ) = 0.3 MGD

Minutes of operation of Primary WAS pump per hour (TWASp) = 25

Total flow entering Aeration Basins (MGD) 
	= 1.2 + (50,000 . 10-6) – 0.2 – (80 . 25 . 24 . 10-6)  + 0.3

= 1.3 MGD

Note - if you don’t run your WAS pumps every hour, follow the calculation below:

TWAS (mins/hr) = Total hours of operation per day x 60 / 24

Total hours of operation per day : 8
	TWAS = 8 x 60 / 24 = 20 mins / hr

Step (ii) : Calculating total BOD entering Aeration Basins
Amount of BOD (lbs/day) = Total Flow (MGD) x BOD conc (mg/L) x 8.34

Total Flow entering Aeration Basins : 1.3 MGD

BOD concentration : 250 mg/L

Amount of BOD entering Aeration Basins = 1.3 x 250 x 8.34 = 2711 lbs/day

Step (iii) : Calculating OLR
OLR (lbs/day / 1000 gal) = 
Amount of BOD (lbs/day) / (Total Volume of Aeration Basins (million gal) x 1000)

Amount of BOD entering Aeration Basins : 2711 lbs/day

Total Volume of Aeration Basins : 0.75 million gal

OLR = 2711 / (0.75 x 1000) = 3.6 lbs/day / 1000 gal

- Next step:

In the next page, you will have to input the average of your calculated OLR for all Aeration Basins in service. Jarvis will use this input to test or check if it’s a sign of a problem within your facility.

- Further Reading:

For a detailed understanding of BOD - concept, monitoring and calculation, refer to the section below.

Notes on BOD (Biochemical Oxygen Demand)

- What is BOD?

(Source: USGS) 
BOD stands for Biochemical Oxygen Demand. It is a measure of how much food in the form of organic matter or substrate there is in your wastewater. This is expressed as an oxygen demand or the amount of oxygen required by bacteria to digest the food.

- About the BOD5 Test:

The BOD test measures the change in DO (Dissolved Oxygen) concentration in wastewater samples, over a given period of time at a specified temperature.

There are two stages of decomposition in the BOD test : a carbonaceous stage and a nitrogenous stage. The carbonaceous stage, or first stage, represents that portion of oxygen demand involved in the conversion of organic carbon to carbon dioxide. The nitrogenous stage, or second stage, represents a combined carbonaceous plus nitrogenous demand, when organic nitrogen, ammonia, and nitrite are converted to nitrate. Nitrogenous oxygen demand generally begins after about 6 days. 20 days is considered, by convention, adequate time for a complete biochemical oxidation of organic matter (ultimate BOD or BODu), but this is often impractical since BOD data is a basic monitoring requirement to address any immediate concerns.

The standard oxidation (or incubation) test period for BOD is 5 days at 20°C (BOD5), to measure specifically the carbonaceous demand or CBOD. Since wastewater contains ammonia, nitrite and nitrifying bacteria, it’s likely for nitrification to occur in less than 5 days and distort your BOD5. In this case, a chemical compound that prevents nitrification should be added to the sample.

A detailed explanation of the BOD test is provided further below.

- What are measurement units of BOD?

BOD is measured in mg/L or ppm (parts per million).

- How do you calculate BOD after doing the BOD test?
BOD5 (mg/L) = (D1 - D2) / P

Where,
D1: Initial DO concentration on Day 0

D2: Initial DO concentration on Day 5

P: Decimal volumetric fraction of sample used (for example, if you diluted 5 mL of sample to 300 mL => P = 5 / 300 = 0.0167

Example:

DO concentration on Day 0 : 8 mg/L

DO concentration on Day 5 : 2 mg/L

Wastewater used : 5 mL, diluted to 300 mL

BOD5 (mg/L) 
= (D1 - D2) / P
= (8 - 2) / (5 / 300)
= 359 mg/L

Detailed explanation of BOD test

- What are requirements for sampling, storage and sample preparation for the BOD5 test?

The procedure is elaborated below (Source: USGS). For more details, refer to APHA Standard Method: 5210B

- Equipment required

- Constant-temperature chamber or water bath

- Aquarium pump, plastic air tubing, and air diffusion stones : 
Wash tubing and air diffusion stone thoroughly with a 0.2-percent nonphosphate detergent solution and rinse thoroughly 3 to 5 times with deionized or distilled water before use

- BOD bottles (300 mL) : 
Wash bottles thoroughly with a 0.2- percent nonphosphate detergent solution and rinse with deionized or distilled water before each test. Label bottles appropriately for sample identification.

- Glass beads : 
Wash thoroughly with a 0.2- percent nonphosphate detergent solution and rinse with deionized or distilled water before use.

- Graduated cylinder

- Overcap

- Pipette

- Thermometer

- Sample container(s)

- Waste disposal container(s)

- Reagents required

- Calcium chloride (CaCl2) solution :
Dissolve 27.5 g in deionized water and dilute to 1 L

- Dilution water : 
Deionized water of high quality; must be free from toxic substances such as chlorine or toxic metals.

- Ferric chloride (FeCl3.6H2O) solution :
Dissolve 0.25 g in deionized water and dilute to 1 L

- Magnesium sulfate (MgSO4.7H2O) solution :
Dissolve 22.5 g in deionized water and dilute to 1 L

- Phosphate buffer solution :
Dissolve the following in 500 mL of ionized water and dilute to 1 L:

  - 8.5 g of KH2PO4

  - 21.8 g of KHPO4

  - 33.4 g of Na2HPO4.7H2O

  - 1.7 g of NH4Cl

- Sodium hydroxide (NaOH) for caustic acidity pretreatment :
Add 40 g of NaOH to about 900 mL of deionized water. Mix and dilute to 1 L (1 N NaOH). Store in a plastic container.

- Sodium sulfite (Na2SO3) or sodium thiosulfate (Na2S2O3) for residual chlorine pretreatment solution :
Dissolve 1.575 g of Na2SO3 or NaS2O3 in 1 L of deionized water. This solution is not stable and should be prepared daily to weekly, as needed. Store refrigerated in a dark bottle.

- Cobalt chloride (CoCl3) crystals for for zero DO calibration solution

- Sulfuric acid (H2SO4) for caustic alkalinity pretreatment :
Slowly and while stirring add 28 mL of concentrated H2SO4 to about 900 mL of deionized water. Mix and dilute acid solution to 1 L (1 N H2SO4)

Note of precaution: Properly discard chemical reagents if there is any sign of biological growth or if past the expiration date

- DO instrumentation required

- Calibration chamber (Follow manufacturer’s recommendations)

- DO instrument system (Temperature and pressure compensated)

- Stirrer attachment for DO sensor

- Pocket altimeter-barometer

- DO sensor membrane replacement kit (Membranes, O-rings, KCl filling solution)

- Zero DO calibration solution (Dissolve 1 g Na2SO3 and a few crystals of CoCl3 in 1 L water. Prepare fresh zero DO solution before each use)

- Sample collection and storage
Samples can degrade significantly during extended storage. To minimize sample degradation, and thus avoid negative bias in the measurement of BOD5, note the following:

- Analyze samples promptly or

- Store chilled without freezing (maintain a temperature from 1 to 4°C) - chilling the sample is not necessary if the analysis begins within 2 hours of collection
The maximum holding time of a sample to be analyzed for BOD is 24 hours.

- Recommended approach : Start the BOD5 analysis immediately after sample collection to minimize changes in bacterial concentration.

- If a sample is refrigerated prior to analysis, allow the sample to warm to 20°C before starting the test. A sample may be removed from an ice chest or refrigerator during transit to allow it to warm to 20°C before analysis begins.

- Sample preparation

- A BOD5 value greater than 7 mg/L requires sample dilution. Dilution is necessary when the amount of DO consumed by microorganisms is greater than the amount of DO available in the air-saturated BOD5 sample. Refer to the following recommended sample volumes (Sawyer and McCarty) for your anticipated range of BOD variation, and dilute to 300 mL :

  - 0-7 mg/L BOD => 300 mL sample

  - 6-21 mg/L BOD => 100 mL sample

  - 12-42 mg/L BOD => 50 mL sample

  - 30-105 mg/L BOD => 20 mL sample

  - 60-210 mg/L BOD => 10 mL sample

  - 120-420 mg/L BOD => 5 mL sample

  - 300-1050 mg/L BOD => 2 mL sample

  - 600-2100 mg/L BOD => 1 mL sample

BOD5 values are acceptable only if the following criteria are met:

- The DO concentration after 5 days must be at least 1 mg/L and at least 2 mg/L lower in concentration than the initial DO

- At least three different dilutions are set per sample to cover the anticipated range of BOD. The three sample volumes used are selected to provide an overlapping range in expected BOD concentrations. For example, if the BOD5 is known to range from 3 to 28 mg/L, then the sample volumes used for the test would be 50 mL, 100 mL, and 300 mL (no dilution). If there is no prior knowledge of the BOD5, use a minimum of four volumes to accommodate a range of BOD5 from 0 to 210 mg/L.

- Prepare dilution water 3 to 5 days before initiating the BOD5 tests to ensure that the BOD of the dilution water is less than 0.2 mg/L. Discard dilution water if there is any sign of biological growth.

- Determine sample pH. Adjust sample to a pH between 6.5 and 7.5, using either sulfuric acid (H2SO4) to reduce pH or sodium hydroxide (NaOH) to raise pH.

- Add Sodium sulfite (Na2SO3) to remove residual chlorine, if necessary. Samples containing toxic metals, arsenic, or cyanide will require special study and pretreatment. Refer to APHA for guidance on the same.

Note of precaution:
Some types of sewage, such as untreated industrial wastes, disinfected wastes, and wastes that have been heated to a high temperature contain too few bacteria to perform the test. Thus, the samples must be seeded with a population of microorganisms to produce an oxygen demand. For guidance on seeding procedures, refer APHA.

- What is the laboratory procedure for BOD measurement? (detailed)
The procedure is elaborated below (Source: USGS). For more details, refer to APHA Standard Method: 5210B

- Determine the amount of sample to be analyzed. Use the historical results, if available, of a previous test of BOD5 for a particular sampling site.

- Place a clean, calibrated thermometer into the constant temperature chamber.

- Turn on the constant temperature chamber to allow the controlled temperature to stabilize at 20°C ±1°C

- Aerate dilution water using DO instrumentation before adding nutrient solutions.

- After aeration,

- Add to dilution water 1 mL each of the potassium phosphate, magnesium sulfate, calcium chloride, and ferric chloride solutions per 1 L of dilution water

- Shake the container of dilution water for about 1minute to dissolve the slurry and to saturate the water with oxygen

- Place the dilution water in the constant temperature chamber to maintain a temperature of 20°C until sample dilutions and analyses begin

- The initial and final (after 5 days ± 4 hours) DO tests of the dilution water are determined and recorded simultaneously with each batch of environmental samples.

- Check the temperature of the air incubator or water bath using a laboratory thermometer to ensure that the temperature has been maintained at 20° ± 1°C

- Place the sample container in the constant-temperature chamber or water bath to begin warming the sample to 20°C ± 1°C. While the sample is warming, insert the air diffusion stone into the container and aerate the sample for about 15 minutes. After removing the air diffusion stone, allow several minutes for excess air bubbles to dissipate. The initial DO of the BOD sample needs to be at or slightly below saturation.

- Prepare dilutions as required—Measure the appropriate amounts of sample necessary for the analysis. BOD5 dilutions should result in a DO residual of at least 1 mg/L and a DO depletion of at least 2 mg/L after a 5-day incubation to produce the most reliable results. Prepare the dilutions to obtain a DO uptake in this range using the dilution water prepared earlier.

- Calibrate the DO instrument per procedures specified by the manufacturer.

- After bringing the samples to saturation and preparing the dilutions (steps 8 and 9 above), measure the initial DO concentration (D1) of each sample and each dilution blank.

- Carefully insert the self-stirring sensor into the BOD bottle, avoiding air entrapment.

- Turn on the stirrer and allow 1 to 2 minutes for the DO and temperature readings to stabilize.

- Turn off the stirrer and remove the sensor from the BOD bottle. Rinse the sensor and stirrer with deionized water from a wash bottle. Discard rinse water into a waste container.

- Add glass beads to the BOD bottle, if necessary, to displace the sample up to the neck of the bottle so that inserting a glass stopper will displace all air, leaving no bubbles.

- Carefully cap the BOD bottle with the ground-glass stopper. Tip the bottle to one side and check for an air bubble.

- If an air bubble is present, add glass beads to the bottle until the bubble is removed. Cap the bottle and check again for an air bubble. Repeat if necessary.

- If no bubble is present in the sample, create a water seal by adding distilled or deionized water to the top of the BOD bottle around the glass stopper. Then place the overcap over the stopper on the BOD bottle to minimize evaporation from the water seal.

- Place the sealed BOD sample in the air incubator or water bath and incubate the sample at 20°C ± 1°C for 5 days.

- At the end of 5 days ± 4 hours, remove the BOD bottles from the incubator, remove the overcap, pour off the water seal, remove the ground-glass stopper, and measure the final DO concentration

- The DO uptake (from 0 to 5 days) in the dilution water should not be greater than 0.2 mg/L and preferably not more than 0.1 mg/L. Exceeding the 0.2-mg/L criterion could be grounds for rejecting results of the BOD analysis of the environmental sample

- Dilution water of poor quality will cause an oxygen demand and appear as sample BOD. Improve purification or get the dilution water from another source if DO uptake exceeds 0.2 mg/L

Note for Quality Control: 
The BOD5 test can be quite variable. Collect sufficient field and split replicates (10 to 20 percent) to provide an estimate of method variability.