Read Me for key understanding (Concept, Target Range, Calculation)

Solids Loading Rate (SLR) - Secondary Clarifiers

- About this test

This document serves as guidance to determine the Solids Loading Rate (SLR) for Aeration Basins. Essential information is presented in the form of Q&A in the sections below. In the next page, you will have to enter the average SLR for all Secondary Clarifiers in service.

- What is SLR?

Solids Loading Rate (SLR) is the rate of solids or bugs being loaded into your Secondary Clarifiers per unit surface area of the clarifiers. SLR is related to SOR (Surface Overflow Rate) in that SLR measures the amount of solids being loaded, while SLR measures the hydraulic load (volume of water).

- Why is SLR an important parameter?

SLR is indicative of whether you’re loading your clarifiers optimally for the capacity available, to be able to separate the solids and liquid effluent.

- The amount of solids being loaded relative to the capacity or surface area, affects settling characteristics and solid-liquid separation

- If your SLR is too high, it means your clarifier is overloaded with solids. As a result, they will fail to settle and wash out over the weirs, causing an increase in the effluent TSS.

- The same could happen if your SLR is too low, meaning an underloaded clarifier. In this situation, there may not be enough flocs created to aggregate and settle down, causing your effluent to appear cloudy.

- The idea is to provide just enough SLR, so you can allow solids enough time to settle, while keeping the flow going and maximizing the influent flow you receive.

- What are measurement units of SLR?

SLR is measured in lbs / day / sq. ft.

- What is an ideal range of SLR?
12 to 50 lbs / day / sq.ft

- How do you measure or calculate SLR?

SLR (lbs/ day/ sq.ft) =

Total flow entering Secondary Clarifiers (MGD) x

MLSS (mg/L) x 8.34 / Total Surface Area of Secondary Clarifiers (sq. ft)

Monitoring locations for determining SLR:

- Aeration Basin : Monitoring for MLSS concentration

- Secondary Clarifier : Monitoring for incoming flow

- RAS, WAS lines : Monitoring for flow

Sample Calculation:
Total Flow entering Secondary Clarifiers : 1.3 MGD

MLSS concentration : 2500 mg/L

Surface area of clarifier : 800 sq.ft

SLR = 1.3 x 2500 x 8.34 / 800

SLR = 34 lbs / day / sq.ft

A detailed calculation is provided further below.

- What are factors that affect SLR?

SLR (lbs/ day/ sq.ft) =

Total flow entering Secondary Clarifiers (MGD) x

MLSS (mg/L) x 8.34 / Total Surface Area of Secondary Clarifiers (sq. ft)

- As seen in the formula, the SLR is affected by the spatial extent (surface area) of the secondary clarifier, the speed (rate) of flow entering the secondary clarifier and the MLSS concentration (Mixed Liquor Suspended Solids concentration).

- For a fixed rate of flow entering the clarifier, if you increase the spatial extent (surface area) of the secondary clarifier, the SLR decreases. Decreasing the surface area increases the SLR.

- For a fixed surface area and MLSS concentration, if you slow down the flow, the SLR decreases. Speeding up the flow increases the SLR.

- For a fixed flow rate, if you increase the MLSS concentration, the SLR increases due to excess solids. Reducing the MLSS concentration for the same flow rate, decreases the SLR.

- Your design should provide for the ideal SLR by striking a balance between maximum surface area utilization, maximum influent rate of flow and optimum MLSS (or SRT affecting MLSS).

- Things to keep in mind to ensure accurate calculation of SLR:

- Ensure you account for all flows entering each Secondary Clarifier or leaving each Aeration Basin, as demonstrated in the calculation steps

- Ensure your flowmeters are cleaned and calibrated from time to time

- Ensure regular monitoring and accurate measurement of MLSS

- Further corrective actions for secondary clarifiers, if required, will be specified in the Troubleshooting section

- Detailed Calculation of SLR:

SLR (lbs/ day/ sq.ft) =

Total flow entering Secondary Clarifiers (MGD) x

MLSS (mg/L) x 8.34 / Total Surface Area of Secondary Clarifiers (sq. ft)

Step (i) : Calculating total flow entering Secondary Clarifier
You can determine the flow through a flow meter that measures the amount of flow leaving each Aeration Basin or entering each Secondary Clarifier, OR

Derive it from known flows demonstrated below.

Total flow =

FRaw + (FFil . 10-6) – FD – (FWASp . TWASp . 24 . 10-6) + FRAS

where,

Total flow : Total flow entering Secondary Clarifier (MGD)
	FRaw : Total raw influent flow received by your facility (MGD)

FFil : Filtrate from Sludge thickening, dewatering (GPD or gal per day)

FD : Diverted Sidestream flow bypassing Secondary Treatment (MGD)

FWASp : Primary WAS Flow (GPM or gal per min)

FRAS : RAS Flow (MGD)

TWASp : Minutes of operation of Primary WAS pump per hour, on average

Example:
	Raw influent flow (FRaw) = 1.2 MGD

Filtrate from Sludge thickening, dewatering (FFil) = 50,000 GPD

Diverted Sidestream flow bypassing Secondary Treatment (FD) = 0.2 MGD
	Primary WAS Flow (FWASp) = 80 GPM

RAS Flow (FRAS ) = 0.3 MGD

Minutes of operation of Primary WAS pump per hour (TWASp) = 25

Total flow entering Secondary Clarifier (MGD) 
	= 1.2 + (50,000 . 10-6) – 0.2 – (80 . 25 . 24 . 10-6) + 0.3

= 1.3 MGD

Note - if you don’t run your WAS pumps every hour, follow the calculation below:

TWAS (mins/hr) =

Total hours of operation per day x 60 / 24

Total hours of operation per day : 8
	TWAS = 8 x 60 / 24 = 20 mins / hr

Step (ii) : Calculating SLR
SLR (lbs/ day/ sq.ft) =

Total flow entering Secondary Clarifiers (MGD) x

MLSS (mg/L) x 8.34 / Total Surface Area of Secondary Clarifiers (sq. ft)

Total Flow entering Secondary Clarifiers : 1.3 MGD

MLSS concentration : 2500 mg/L

Surface area of clarifier : 800 sq.ft

SLR = 1.3 x 2500 x 8.34 / 800

SLR = 34 lbs / day / sq.ft

Note - To determine the Surface Area of your Clarifier, follow the calculation below:
	
	For circular clarifiers:

Surface Area (sq.ft) = (22/7) x (1/4) x (Diameter)^2

Diameter : 30 ft.

Surface Area = (22/7) x (1/4) x (30)^2 = 707 sq.ft

For rectangular clarifiers:

Surface Area (sq.ft) = Length x Width

Length : 30 ft.

Width : 25 ft.

Surface Area = 30 x 25 = 750 sq.ft

- Next step:

In the next page, you will have to input the average of your calculated SLR for all Secondary Clarifiers in service. Jarvis will use this input to test or check if it’s a sign of a problem within your facility.

- Further Reading:

For a detailed understanding of MLSS - concept, monitoring and calculation, refer to the section below.

Notes on MLSS and MLVSS

- What are MLSS and MLVSS?

- MLSS stands for Mixed Liquor Suspended Solids. This is the average TSS of the water or ‘mixed liquor’ (it is called mixed liquor because of the mixing of the Raw Influent, RAS and the bugs in the reactor).

- MLVSS stands for Mixed Liquor Volatile Suspended Solids. This is the volatile component of MLSS, that is made up of living microorganisms, floating in the water. The rest of the MLSS is inert.

- What’s the difference between TSS, MLSS and MLVSS?

- TSS stands for Total Suspended Solids concentration. It measures the amount of solids floating or suspended (not dissolved) in a certain quantity of water. In other words, it measures the concentration of suspended solids that are over 2 microns in size. TSS could include inert solids like sand and clay, or living (volatile) solids like bacteria and other bugs.

- TSS is the general term, while MLSS refers to the TSS within the Aeration Basins present as mixed liquor.

- MLVSS is the volatile component of MLSS, like VSS is the volatile component of TSS.

- What are measurement units of MLSS and MLVSS?

TSS, MLSS and MLVSS are measured in mg/L or ppm (parts per million).

- How do you measure or calculate MLSS and MLVSS?

MLSS determination:

- Digital measurement - TSS sensors or monitors

- Lab Test (Gravimetric Filtration) - Standard Methods 2540 D, APHA

- Decanter Centrifuge

These are explained in further detail below. Choose the method that works for you.

MLVSS determination:
MLVSS can only be determined using the Lab Test mentioned above, which will be explained further. From the MLSS and MLVSS values, you can determine an average MLVSS / MLSS ratio. If the composition of your total solids is generally stable, you can use the average MLVSS / MLSS ratio in your process calculations, instead of having to measure MLVSS each time.

- Methods to determine MLSS and MLVSS:

I. Digital measurement - TSS sensors or monitors (only MLSS)

About this method:

- There are portable, hand-held meters, sensors, monitors and analyzers available in the market for measuring TSS and a host of other polluting parameters.

- Advantages: Accurate, Saves time and money in the long run, considering TSS is a critical parameter you have to keep monitoring regularly.

- Disadvantages: Electronic device might malfunction, probes could lose sensitivity, require calibration, etc.

Procedure:

- Make sure your probes are rinsed and dried before use. Monitor for TSS at a handful of locations in the vicinity. The readings shouldn't fluctuate (change) too much. Your monitoring locations should have :

  - Well-mixed water (the water looks uniform)

  - Steady flow, not violent (turbulent)

  - No accumulation (build-up) of sediments

Precautions / Sources of Error:

- Make sure to test for TSS correctly as described above. The monitoring location must be uniform (homogenous), so it can be representative.

- Keep the probes clean. Rinse and dry them regularly.

- Check the technical manual for guidance on maintenance and calibration.

Final Calculation:

Read from meter.

Report as TSS or MLSS (for Aeration Basins) : ______ mg/L

II. Lab Test (Gravimetric Filtration) - for MLSS and MLVSS
Standard Methods 2540D, APHA ; USGS I-3765-85; EPA Method 160.2

About this method:

- The sample (whole bottle sample or well mixed sub-sample) is filtered, with rinsing, through a pre-weighed glass fiber filter, and the residue on the filter is dried to constant weight at 103-105℃.

- Advantages: Established method, Cheaper

- Disadvantages: More chances of error, Takes more time and effort

Procedure:

- Sampling : Make sure your sampling containers are rinsed, dried and labeled before use. Monitor for TSS at a handful of locations in the vicinity. Your monitoring locations should have :

  - Well-mixed water (the water looks uniform)

  - Steady flow, not violent (turbulent)

  - No accumulation (build-up) of sediments

- Apparatus & Materials required : Sampling containers, Glass-fiber filter, Wide-bore pipet, Graduated cylinder, Forceps, Dessicator, Muffle Furnace or Convection Oven, Vacuum suction flask, Analytical Balance, Distilled or Deionized water

- Method:

- Pre-wash glass fiber filters (nominal 1.5 μm pore size) with deionized water, bake at 103-105°C (or hotter) for at least 1 hour

- Pre-weigh the filter paper using an analytical balance. Record this weight in mg as M0.

- Make the water samples uniform by vigorously mixing well just before sub-sampling (or use the whole bottle if whole bottle sampling is requested)

- Accurately measure the required sample volume (recommended: 25 mL), and transfer to a filtration apparatus containing a pre-weighed filter. Record this volume in liters as V. For eg, if the volume is 25 mL, record V as 0.025 L.

- Rinse filter with 3 volumes of 10 mL deionized water, or as-required to ensure full rinsing of dissolved salts from all portions of the filter paper using the selected apparatus.

- Leave the filter in the muffle furnace or convection oven at 103° - 105°C for 24 hours.

- Remove and cool inside a dessicator for 15 mins.

- Accurately measure the post-weight of the filter. Record this weight in mg as M1.

- Use the following equation to calculate MLSS in mg/L.

MLSS (mg/L) = (M1 - M0) x 1000 / V
where,
M0 = Weight of tared filter, in mg
M1 = Weight of tared filter, with the dried residue, in mg after heating at 103° - 105°C

V = Volume of sample, in Liters

- Now, set the muffle furnace to 550°C for 2 hours and repeat the steps above. The higher temperature evaporates volatile solids, leaving inserts behind. This time, allow the filter papers to cool in the dessicator for 30 mins.

- Accurately measure the post-weight of the filter. Record this weight in mg as M2.

- Use the following equation to calculate MLVSS in mg/L.

MLVSS (mg/L) = (M1 - M2) x 1000 / V
where,
M1 = Weight of tared filter, with the dried residue, in mg, after heating at 103° - 105°C

M2 = Weight of tared filter, with the dried residue, in mg, after heating at 550°C

V = Volume of sample, in Liters

For NPDES or CWA reporting, consult Standard Methods for the Examination of Water and Wastewater, 2540D or USGS I-3765-85 or EPA Method 160.2.

Precautions / Sources of Error:

- Make sure to sample for TSS correctly as described above. The monitoring location must be uniform (homogenous), so it can be representative.

- Make sure your containers and appartus are always cleaned, rinsed with deionized water, and dried before use.

- Sample temperature should be chilled to ≤ 10℃ immediately after sampling and during transit to the laboratory. In the laboratory, samples must be refrigerated at ≤ 6℃. Avoid freezing to prevent sample breakage.

- Choosing the right filter : Filtration must utilize a glass fiber filter with nominal pore size of ~ 1.5 μm, e.g. using filters such as Whatman 934AH, Gelman A/E, Millipore AP40, Ahlstrom 161, Environmental Express Pro Weigh, or equivalent.

- Drying of filters must be conducted at 103 - 105℃.

- Make sure to transfer the effluent sample gently between appartus.

- Make sure your vacuum suction flask is functioning consistently well.

- Identify any sample that yields a residue mass < 2.5 mg or > 200 mg and report the results as an “estimate” because the mass has exceeded the criteria of this analysis.

III. Decanter Centrifuge

About this method:

- Centrifugation is a technique used to separate phases of different densities.

- Advantages: Convenient, Fast, Can be used to analyze a large number of samples.

- Disadvantages: Susceptible to errors as accuracy is affected by sludge compact-ability

Procedure:

- Sampling : Make sure your sampling containers are rinsed, dried and labelled before use. Monitor for MLSS at a handful of locations in the Aeration Basin. Your monitoring locations should have :

  - Well-mixed water (the water looks uniform)

  - Steady flow, not violent (turbulent)

  - No accumulation (build-up) of sediments

- Apparatus & Materials required : Sampling container, Centrifuge tubes, Decanter Centrifuge Rotor, Transfer pipette, Conical flasks, Analytical balance

- Method :

  - Draw 15 mL aliquot from a well-mixed container

  - Centrifuge for ten minutes at 2000 or 4000 rpm

  - Pour off supernatant, separating and drying the retained solids

  - Weigh the solids

Precautions / Sources of Error:

- Make sure to sample for MLSS correctly as described above. The monitoring location must be uniform (homogenous), so it can be representative.

- Make sure your containers and appartus are always cleaned, rinsed with deionized water, and dried before use.

- Sample temperature should be chilled to ≤ 10℃ immediately after sampling and during transit to the laboratory. In the laboratory, samples must be refrigerated at ≤ 6℃. Avoid freezing to prevent sample breakage.

- Use polypropylene centrifuge tubes with a blue screw cap, not white. Never use glass test tubes.

- Screw on the tube tightly. Check cap for cracks or protrusions.

- Do not fill the centrifuge tube beyond 10 mL.

- When loading your samples into the rotor, ensure it's balanced. Tubes of equal weight must be loaded opposite each other. Use water if you don't have another sample to balance the weight.

- Check the technical manual or project guide to know how long the rotor should run, and for guidance on maintenance.

- Don't remove the tubes quickly or shake them violently. Remove the supernatant carefully without disturbing the residue at the bottom.

Final Calculation:

MLSS (mg/L) = 4200 x Centrifuge tube reading (mL)

* Note: The conversion factor (K value) of 4200 is an approximate average. You can determine this more accurately by graphing out different MLSS (mg/L) values determined using the other two methods, and different Centrifuge tube readings (mL) to get the exact correlation.

Report as MLSS : ______ mg/L