Read Me for key understanding (Concept, Target Range, Calculation)

F/M Ratio (Food-to-Microorganism Ratio)

- About this test

This document serves as guidance to determine the F/M Ratio for Aeration Basins. Essential information is presented in the form of Q&A in the sections below. In the next page, you will have to enter the average F/M Ratio for all Aeration Basins in service.

- What is F/M Ratio?

The F/M ratio (Food/Microorganism ratio) is a measure of how much food (BOD) is coming in relative to the population of microorganisms (MLVSS) in your Aeration Basins. This is a critical process parameter for your facility.

- Why is F/M Ratio an important parameter?

- The wastewater your facility receives has organic waste which is food for the bugs in your system. The bugs digest the waste and settle down, making the water clean enough to discharge. But this happens at an optimum balance (ratio) of food incoming to the microorganism populations. So, maintaining the right F/M ratio is the key to optimizing your facility’s treatment efficiency.

- F/M ratio being too high or too low will cause process upsets and excess TSS in the effluent, leading to permit violations.

- What are measurement units of F/M Ratio?

F/M Ratio is an index, with F (food) measured in lbs of BOD/day and M (microorganism) measured in lbs of MLVSS

- What is an ideal range of F/M Ratio?
Conventional Activated Sludge (complete mix) : 0.2 - 0.6

Contact Stabilization : 0.15 - 0.2

Extended Aeration : 0.01 - 0.07
Step Aeration : 0.2 - 0.5
Two-Stage Aeration : 0.07 - 0.15

- How do you calculate F/M Ratio?

F/M Ratio = BOD (lbs/day) / MLVSS (lbs)

=>

F/M Ratio =

Total flow entering Aeration Basins (MGD) x BOD (mg/L) /

(MLVSS (mg/L) x Total Volume of Aeration Basins (million gal))

Monitoring locations for determining F/M Ratio:

- Aeration Basins: Monitoring for influent flow, influent BOD,

Sample Calculation:
Total Flow entering Aeration Basin : 1.3 MGD

Influent BOD conc. : 250 mg/L

Volume of Aeration Basin : 0.75 million gal

MLVSS concentration : 1800 mg/L
F/M Ratio = 1.3 x 250 / (1800 x 0.75)

F/M Ratio = 0.24

A detailed calculation is provided further below.

- What are factors that affect F/M Ratio?

F/M Ratio = BOD (lbs/day) / MLVSS (lbs)

=>

F/M Ratio =

Total flow entering Aeration Basins (MGD) x BOD (mg/L) /

(MLVSS (mg/L) x Total Volume of Aeration Basins (million gal))

- As seen in the formula, F/M Ratio is affected by four factors:
Numerators:

  - Influent flow => Higher flow, means higher F/M ratio and vice versa

  - Influent BOD conc. => Higher BOD, means higher F/M ratio and vice versa

Denominators:

  - MLVSS => Higher MLVSS, means lower F/M and vice versa

  - Volume of Aeration Basins => Higher Volume, means lower F/M and vice versa

- Your design should provide for the ideal F/M Ratio by maintaining the right amount of microorganisms within Aeration Basins, through correct process controls like sludge wasting rates, aeration, etc.

- The extent of pollutant loading may cause variability in F/M Ratio, requiring changes in process configuration.

- Things to keep in mind to ensure accurate calculation of F/M Ratio:

- Ensure you account for all flows entering the Aeration Basins

- Ensure your flowmeters are cleaned and calibrated from time to time

- Further corrective actions, if required, will be specified in the Troubleshooting section

- Detailed Calculation:

F/M Ratio = BOD (lbs/day) / MLVSS (lbs)

Step (i) : Calculating total flow entering Aeration Basins
You can determine the influent flow through a flow meter, or derive it from known flows demonstrated below.

Total flow = FRaw + (FFil . 10-6) – FD – (FWASp . TWASp . 24 . 10-6) + FRAS

where,

Total flow : Total flow entering Aeration Basins (MGD)
	FRaw : Total raw influent flow received by your facility (MGD)

FFil : Filtrate from Sludge thickening, dewatering (GPD or gal per day)

FD : Diverted Sidestream flow bypassing Secondary Treatment (MGD)

FWASp : Primary WAS Flow (GPM or gal per min)

FRAS : RAS Flow (MGD)

TWASp : Minutes of operation of Primary WAS pump per hour, on average

Example:
	Raw influent flow (FRaw) = 1.2 MGD

Filtrate from Sludge thickening, dewatering (FFil) = 50,000 GPD

Diverted Sidestream flow bypassing Secondary Treatment (FD) = 0.2 MGD
	Primary WAS Flow (FWASp) = 80 GPM

RAS Flow (FRAS ) = 0.3 MGD

Minutes of operation of Primary WAS pump per hour (TWASp) = 25

Total flow entering Aeration Basins (MGD) 
	= 1.2 + (50,000 . 10-6) – 0.2 – (80 . 25 . 24 . 10-6)  + 0.3

= 1.3 MGD

Note - if you don’t run your WAS pumps every hour, follow the calculation below:

TWAS (mins/hr) = Total hours of operation per day x 60 / 24

Total hours of operation per day : 8
	TWAS = 8 x 60 / 24 = 20 mins / hr

Step (ii) : Calculating total BOD entering Aeration Basins
Amount of BOD (lbs/day) = Total Flow (MGD) x BOD conc (mg/L) x 8.34

Total Flow entering Aeration Basins : 1.3 MGD

BOD concentration : 250 mg/L

Amount of BOD entering Aeration Basins = 1.3 x 250 x 8.34 = 2711 lbs/day

Step (iii) : Calculating MLVSS
Amount of MLVSS (lbs) = 
Total Volume of Aeration Basins (million gal) x Avg. MLVSS (mg/L) x 8.34

Total Volume of Aeration Basins : 0.75 million gal

MLVSS concentration : 1800 mg/L

Note: If you have a stable avg. MLVSS / MLSS ratio, you can determine MLVSS as follows:

MLVSS = MLSS x (MLVSS / MLSS Ratio)

For eg,

If MLSS = 3000 mg/L

MLVSS / MLSS Ratio = 0.6

=> MLVSS = 3000 x 0.6 = 1800 mg/L

Amount of MLVSS = 0.75 x 1800 x 8.34 = 11,259 lbs

Step (iv) : Calculating F/M Ratio

F/M Ratio = BOD (lbs/day) / MLVSS (lbs)

From step ii and iii,

F/M Ratio = 2711 / 11259 = 0.24

- Next step:

In the next page, you will have to input the average of your average calculated F/M Ratio for all Aeration Basins in service. Jarvis will use this input to test or check if it’s a sign of a problem within your facility.

- Further Reading:

For a detailed understanding of BOD and MLVSS - concept, monitoring and calculation, refer to the section below.

Notes on BOD (Biochemical Oxygen Demand) and MLVSS (Mixed Liquor Volatile Suspended Solids)

- What is BOD?

(Source: USGS) 
BOD stands for Biochemical Oxygen Demand. It is a measure of how much food in the form of organic matter or substrate there is in your wastewater. This is expressed as an oxygen demand or the amount of oxygen required by bacteria to digest the food.

- What are MLSS and MLVSS?

- MLSS stands for Mixed Liquor Suspended Solids. This is the average TSS of the water or ‘mixed liquor’ (it is called mixed liquor because of the mixing of the Raw Influent, RAS and the bugs in the reactor).

- MLVSS stands for Mixed Liquor Volatile Suspended Solids. This is the volatile component of MLSS, that is made up of living microorganisms, floating in the water. The rest of the MLSS is inert.

- What’s the difference between TSS, MLSS and MLVSS?

- TSS stands for Total Suspended Solids concentration. It measures the amount of solids floating or suspended (not dissolved) in a certain quantity of water. In other words, it measures the concentration of suspended solids that are over 2 microns in size. TSS could include inert solids like sand and clay, or living (volatile) solids like bacteria and other bugs.

- TSS is the general term, while MLSS refers to the TSS within the Aeration Basins present as mixed liquor.

- MLVSS is the volatile component of MLSS, like VSS is the volatile component of TSS.

- What are measurement units of BOD and MLVSS?

BOD and MLVSS are measured in mg/L or ppm (parts per million).

- About the BOD5 Test:

The BOD test measures the change in DO (Dissolved Oxygen) concentration in wastewater samples, over a given period of time at a specified temperature.

There are two stages of decomposition in the BOD test : a carbonaceous stage and a nitrogenous stage. The carbonaceous stage, or first stage, represents that portion of oxygen demand involved in the conversion of organic carbon to carbon dioxide. The nitrogenous stage, or second stage, represents a combined carbonaceous plus nitrogenous demand, when organic nitrogen, ammonia, and nitrite are converted to nitrate. Nitrogenous oxygen demand generally begins after about 6 days. 20 days is considered, by convention, adequate time for a complete biochemical oxidation of organic matter (ultimate BOD or BODu), but this is often impractical since BOD data is a basic monitoring requirement to address any immediate concerns.

The standard oxidation (or incubation) test period for BOD is 5 days at 20°C (BOD5), to measure specifically the carbonaceous demand or CBOD. Since wastewater contains ammonia, nitrite and nitrifying bacteria, it’s likely for nitrification to occur in less than 5 days and distort your BOD5. In this case, a chemical compound that prevents nitrification should be added to the sample.

A detailed explanation of the BOD test is provided further below.

- How do you calculate BOD after doing the BOD test?
BOD5 (mg/L) = (D1 - D2) / P

Where,
D1: Initial DO concentration on Day 0

D2: Initial DO concentration on Day 5

P: Decimal volumetric fraction of sample used (for example, if you diluted 5 mL of sample to 300 mL => P = 5 / 300 = 0.0167

Example:

DO concentration on Day 0 : 8 mg/L

DO concentration on Day 5 : 2 mg/L

Wastewater used : 5 mL, diluted to 300 mL

BOD5 (mg/L) 
= (D1 - D2) / P
= (8 - 2) / (5 / 300)
= 359 mg/L

- How do you measure or calculate MLSS and MLVSS?

MLSS determination:

- Digital measurement - TSS sensors or monitors

- Lab Test (Gravimetric Filtration) - Standard Methods 2540 D, APHA

- Decanter Centrifuge

These are explained in further detail below. Choose the method that works for you.

MLVSS determination:
MLVSS can only be determined using the Lab Test mentioned above, which will be explained further. From the MLSS and MLVSS values, you can determine an average MLVSS / MLSS ratio. If the composition of your total solids is generally stable, you can use the average MLVSS / MLSS ratio in your process calculations, instead of having to measure MLVSS each time.

- Methods to determine MLSS and MLVSS:

I. Digital measurement - TSS sensors or monitors (only MLSS)

About this method:

- There are portable, hand-held meters, sensors, monitors and analyzers available in the market for measuring TSS and a host of other polluting parameters.

- Advantages: Accurate, Saves time and money in the long run, considering TSS is a critical parameter you have to keep monitoring regularly.

- Disadvantages: Electronic device might malfunction, probes could lose sensitivity, require calibration, etc.

Procedure:

- Make sure your probes are rinsed and dried before use. Monitor for TSS at a handful of locations in the vicinity. The readings shouldn't fluctuate (change) too much. Your monitoring locations should have :

  - Well-mixed water (the water looks uniform)

  - Steady flow, not violent (turbulent)

  - No accumulation (build-up) of sediments

Precautions / Sources of Error:

- Make sure to test for TSS correctly as described above. The monitoring location must be uniform (homogenous), so it can be representative.

- Keep the probes clean. Rinse and dry them regularly.

- Check the technical manual for guidance on maintenance and calibration.

Final Calculation:

Read from meter.

Report as TSS or MLSS (for Aeration Basins) : ______ mg/L

II. Lab Test (Gravimetric Filtration) - for MLSS and MLVSS
Standard Methods 2540D, APHA ; USGS I-3765-85; EPA Method 160.2

About this method:

- The sample (whole bottle sample or well mixed sub-sample) is filtered, with rinsing, through a pre-weighed glass fiber filter, and the residue on the filter is dried to constant weight at 103-105℃.

- Advantages: Established method, Cheaper

- Disadvantages: More chances of error, Takes more time and effort

Procedure:

- Sampling : Make sure your sampling containers are rinsed, dried and labeled before use. Monitor for TSS at a handful of locations in the vicinity. Your monitoring locations should have :

  - Well-mixed water (the water looks uniform)

  - Steady flow, not violent (turbulent)

  - No accumulation (build-up) of sediments

- Apparatus & Materials required : Sampling containers, Glass-fiber filter, Wide-bore pipet, Graduated cylinder, Forceps, Dessicator, Muffle Furnace or Convection Oven, Vacuum suction flask, Analytical Balance, Distilled or Deionized water

- Method:

- Pre-wash glass fiber filters (nominal 1.5 μm pore size) with deionized water, bake at 103-105°C (or hotter) for at least 1 hour

- Pre-weigh the filter paper using an analytical balance. Record this weight in mg as M0.

- Make the water samples uniform by vigorously mixing well just before sub-sampling (or use the whole bottle if whole bottle sampling is requested)

- Accurately measure the required sample volume (recommended: 25 mL), and transfer to a filtration apparatus containing a pre-weighed filter. Record this volume in liters as V. For eg, if the volume is 25 mL, record V as 0.025 L.

- Rinse filter with 3 volumes of 10 mL deionized water, or as-required to ensure full rinsing of dissolved salts from all portions of the filter paper using the selected apparatus.

- Leave the filter in the muffle furnace or convection oven at 103° - 105°C for 24 hours.

- Remove and cool inside a dessicator for 15 mins.

- Accurately measure the post-weight of the filter. Record this weight in mg as M1.

- Use the following equation to calculate MLSS in mg/L.

MLSS (mg/L) = (M1 - M0) x 1000 / V
where,
M0 = Weight of tared filter, in mg
M1 = Weight of tared filter, with the dried residue, in mg after heating at 103° - 105°C

V = Volume of sample, in Liters

- Now, set the muffle furnace to 550°C for 2 hours and repeat the steps above. The higher temperature evaporates volatile solids, leaving inserts behind. This time, allow the filter papers to cool in the dessicator for 30 mins.

- Accurately measure the post-weight of the filter. Record this weight in mg as M2.

- Use the following equation to calculate MLVSS in mg/L.

MLVSS (mg/L) = (M1 - M2) x 1000 / V
where,
M1 = Weight of tared filter, with the dried residue, in mg, after heating at 103° - 105°C

M2 = Weight of tared filter, with the dried residue, in mg, after heating at 550°C

V = Volume of sample, in Liters

For NPDES or CWA reporting, consult Standard Methods for the Examination of Water and Wastewater, 2540D or USGS I-3765-85 or EPA Method 160.2.

Precautions / Sources of Error:

- Make sure to sample for TSS correctly as described above. The monitoring location must be uniform (homogenous), so it can be representative.

- Make sure your containers and appartus are always cleaned, rinsed with deionized water, and dried before use.

- Sample temperature should be chilled to ≤ 10℃ immediately after sampling and during transit to the laboratory. In the laboratory, samples must be refrigerated at ≤ 6℃. Avoid freezing to prevent sample breakage.

- Choosing the right filter : Filtration must utilize a glass fiber filter with nominal pore size of ~ 1.5 μm, e.g. using filters such as Whatman 934AH, Gelman A/E, Millipore AP40, Ahlstrom 161, Environmental Express Pro Weigh, or equivalent.

- Drying of filters must be conducted at 103 - 105℃.

- Make sure to transfer the effluent sample gently between appartus.

- Make sure your vacuum suction flask is functioning consistently well.

- Identify any sample that yields a residue mass < 2.5 mg or > 200 mg and report the results as an “estimate” because the mass has exceeded the criteria of this analysis.

III. Decanter Centrifuge

About this method:

- Centrifugation is a technique used to separate phases of different densities.

- Advantages: Convenient, Fast, Can be used to analyze a large number of samples.

- Disadvantages: Susceptible to errors as accuracy is affected by sludge compact-ability

Procedure:

- Sampling : Make sure your sampling containers are rinsed, dried and labelled before use. Monitor for MLSS at a handful of locations in the Aeration Basin. Your monitoring locations should have :

  - Well-mixed water (the water looks uniform)

  - Steady flow, not violent (turbulent)

  - No accumulation (build-up) of sediments

- Apparatus & Materials required : Sampling container, Centrifuge tubes, Decanter Centrifuge Rotor, Transfer pipette, Conical flasks, Analytical balance

- Method :

  - Draw 15 mL aliquot from a well-mixed container

  - Centrifuge for ten minutes at 2000 or 4000 rpm

  - Pour off supernatant, separating and drying the retained solids

  - Weigh the solids

Precautions / Sources of Error:

- Make sure to sample for MLSS correctly as described above. The monitoring location must be uniform (homogenous), so it can be representative.

- Make sure your containers and appartus are always cleaned, rinsed with deionized water, and dried before use.

- Sample temperature should be chilled to ≤ 10℃ immediately after sampling and during transit to the laboratory. In the laboratory, samples must be refrigerated at ≤ 6℃. Avoid freezing to prevent sample breakage.

- Use polypropylene centrifuge tubes with a blue screw cap, not white. Never use glass test tubes.

- Screw on the tube tightly. Check cap for cracks or protrusions.

- Do not fill the centrifuge tube beyond 10 mL.

- When loading your samples into the rotor, ensure it's balanced. Tubes of equal weight must be loaded opposite each other. Use water if you don't have another sample to balance the weight.

- Check the technical manual or project guide to know how long the rotor should run, and for guidance on maintenance.

- Don't remove the tubes quickly or shake them violently. Remove the supernatant carefully without disturbing the residue at the bottom.

Final Calculation:

MLSS (mg/L) = 4200 x Centrifuge tube reading (mL)

* Note: The conversion factor (K value) of 4200 is an approximate average. You can determine this more accurately by graphing out different MLSS (mg/L) values determined using the other two methods, and different Centrifuge tube readings (mL) to get the exact correlation.

Report as MLSS : ______ mg/L

Detailed explanation of BOD test

- What are requirements for sampling, storage and sample preparation for the BOD5 test?

The procedure is elaborated below (Source: USGS). For more details, refer to APHA Standard Method: 5210B

- Equipment required

- Constant-temperature chamber or water bath

- Aquarium pump, plastic air tubing, and air diffusion stones : 
Wash tubing and air diffusion stone thoroughly with a 0.2-percent nonphosphate detergent solution and rinse thoroughly 3 to 5 times with deionized or distilled water before use

- BOD bottles (300 mL) : 
Wash bottles thoroughly with a 0.2- percent nonphosphate detergent solution and rinse with deionized or distilled water before each test. Label bottles appropriately for sample identification.

- Glass beads : 
Wash thoroughly with a 0.2- percent nonphosphate detergent solution and rinse with deionized or distilled water before use.

- Graduated cylinder

- Overcap

- Pipette

- Thermometer

- Sample container(s)

- Waste disposal container(s)

- Reagents required

- Calcium chloride (CaCl2) solution :
Dissolve 27.5 g in deionized water and dilute to 1 L

- Dilution water : 
Deionized water of high quality; must be free from toxic substances such as chlorine or toxic metals.

- Ferric chloride (FeCl3.6H2O) solution :
Dissolve 0.25 g in deionized water and dilute to 1 L

- Magnesium sulfate (MgSO4.7H2O) solution :
Dissolve 22.5 g in deionized water and dilute to 1 L

- Phosphate buffer solution :
Dissolve the following in 500 mL of ionized water and dilute to 1 L:

  - 8.5 g of KH2PO4

  - 21.8 g of KHPO4

  - 33.4 g of Na2HPO4.7H2O

  - 1.7 g of NH4Cl

- Sodium hydroxide (NaOH) for caustic acidity pretreatment :
Add 40 g of NaOH to about 900 mL of deionized water. Mix and dilute to 1 L (1 N NaOH). Store in a plastic container.

- Sodium sulfite (Na2SO3) or sodium thiosulfate (Na2S2O3) for residual chlorine pretreatment solution :
Dissolve 1.575 g of Na2SO3 or NaS2O3 in 1 L of deionized water. This solution is not stable and should be prepared daily to weekly, as needed. Store refrigerated in a dark bottle.

- Cobalt chloride (CoCl3) crystals for for zero DO calibration solution

- Sulfuric acid (H2SO4) for caustic alkalinity pretreatment :
Slowly and while stirring add 28 mL of concentrated H2SO4 to about 900 mL of deionized water. Mix and dilute acid solution to 1 L (1 N H2SO4)

Note of precaution: Properly discard chemical reagents if there is any sign of biological growth or if past the expiration date

- DO instrumentation required

- Calibration chamber (Follow manufacturer’s recommendations)

- DO instrument system (Temperature and pressure compensated)

- Stirrer attachment for DO sensor

- Pocket altimeter-barometer

- DO sensor membrane replacement kit (Membranes, O-rings, KCl filling solution)

- Zero DO calibration solution (Dissolve 1 g Na2SO3 and a few crystals of CoCl3 in 1 L water. Prepare fresh zero DO solution before each use)

- Sample collection and storage
Samples can degrade significantly during extended storage. To minimize sample degradation, and thus avoid negative bias in the measurement of BOD5, note the following:

- Analyze samples promptly or

- Store chilled without freezing (maintain a temperature from 1 to 4°C) - chilling the sample is not necessary if the analysis begins within 2 hours of collection
The maximum holding time of a sample to be analyzed for BOD is 24 hours.

- Recommended approach : Start the BOD5 analysis immediately after sample collection to minimize changes in bacterial concentration.

- If a sample is refrigerated prior to analysis, allow the sample to warm to 20°C before starting the test. A sample may be removed from an ice chest or refrigerator during transit to allow it to warm to 20°C before analysis begins.

- Sample preparation

- A BOD5 value greater than 7 mg/L requires sample dilution. Dilution is necessary when the amount of DO consumed by microorganisms is greater than the amount of DO available in the air-saturated BOD5 sample. Refer to the following recommended sample volumes (Sawyer and McCarty) for your anticipated range of BOD variation, and dilute to 300 mL :

  - 0-7 mg/L BOD => 300 mL sample

  - 6-21 mg/L BOD => 100 mL sample

  - 12-42 mg/L BOD => 50 mL sample

  - 30-105 mg/L BOD => 20 mL sample

  - 60-210 mg/L BOD => 10 mL sample

  - 120-420 mg/L BOD => 5 mL sample

  - 300-1050 mg/L BOD => 2 mL sample

  - 600-2100 mg/L BOD => 1 mL sample

BOD5 values are acceptable only if the following criteria are met:

- The DO concentration after 5 days must be at least 1 mg/L and at least 2 mg/L lower in concentration than the initial DO

- At least three different dilutions are set per sample to cover the anticipated range of BOD. The three sample volumes used are selected to provide an overlapping range in expected BOD concentrations. For example, if the BOD5 is known to range from 3 to 28 mg/L, then the sample volumes used for the test would be 50 mL, 100 mL, and 300 mL (no dilution). If there is no prior knowledge of the BOD5, use a minimum of four volumes to accommodate a range of BOD5 from 0 to 210 mg/L.

- Prepare dilution water 3 to 5 days before initiating the BOD5 tests to ensure that the BOD of the dilution water is less than 0.2 mg/L. Discard dilution water if there is any sign of biological growth.

- Determine sample pH. Adjust sample to a pH between 6.5 and 7.5, using either sulfuric acid (H2SO4) to reduce pH or sodium hydroxide (NaOH) to raise pH.

- Add Sodium sulfite (Na2SO3) to remove residual chlorine, if necessary. Samples containing toxic metals, arsenic, or cyanide will require special study and pretreatment. Refer to APHA for guidance on the same.

Note of precaution:
Some types of sewage, such as untreated industrial wastes, disinfected wastes, and wastes that have been heated to a high temperature contain too few bacteria to perform the test. Thus, the samples must be seeded with a population of microorganisms to produce an oxygen demand. For guidance on seeding procedures, refer APHA.

- What is the laboratory procedure for BOD measurement? (detailed)
The procedure is elaborated below (Source: USGS). For more details, refer to APHA Standard Method: 5210B

- Determine the amount of sample to be analyzed. Use the historical results, if available, of a previous test of BOD5 for a particular sampling site.

- Place a clean, calibrated thermometer into the constant temperature chamber.

- Turn on the constant temperature chamber to allow the controlled temperature to stabilize at 20°C ±1°C

- Aerate dilution water using DO instrumentation before adding nutrient solutions.

- After aeration,

- Add to dilution water 1 mL each of the potassium phosphate, magnesium sulfate, calcium chloride, and ferric chloride solutions per 1 L of dilution water

- Shake the container of dilution water for about 1minute to dissolve the slurry and to saturate the water with oxygen

- Place the dilution water in the constant temperature chamber to maintain a temperature of 20°C until sample dilutions and analyses begin

- The initial and final (after 5 days ± 4 hours) DO tests of the dilution water are determined and recorded simultaneously with each batch of environmental samples.

- Check the temperature of the air incubator or water bath using a laboratory thermometer to ensure that the temperature has been maintained at 20° ± 1°C

- Place the sample container in the constant-temperature chamber or water bath to begin warming the sample to 20°C ± 1°C. While the sample is warming, insert the air diffusion stone into the container and aerate the sample for about 15 minutes. After removing the air diffusion stone, allow several minutes for excess air bubbles to dissipate. The initial DO of the BOD sample needs to be at or slightly below saturation.

- Prepare dilutions as required—Measure the appropriate amounts of sample necessary for the analysis. BOD5 dilutions should result in a DO residual of at least 1 mg/L and a DO depletion of at least 2 mg/L after a 5-day incubation to produce the most reliable results. Prepare the dilutions to obtain a DO uptake in this range using the dilution water prepared earlier.

- Calibrate the DO instrument per procedures specified by the manufacturer.

- After bringing the samples to saturation and preparing the dilutions (steps 8 and 9 above), measure the initial DO concentration (D1) of each sample and each dilution blank.

- Carefully insert the self-stirring sensor into the BOD bottle, avoiding air entrapment.

- Turn on the stirrer and allow 1 to 2 minutes for the DO and temperature readings to stabilize.

- Turn off the stirrer and remove the sensor from the BOD bottle. Rinse the sensor and stirrer with deionized water from a wash bottle. Discard rinse water into a waste container.

- Add glass beads to the BOD bottle, if necessary, to displace the sample up to the neck of the bottle so that inserting a glass stopper will displace all air, leaving no bubbles.

- Carefully cap the BOD bottle with the ground-glass stopper. Tip the bottle to one side and check for an air bubble.

- If an air bubble is present, add glass beads to the bottle until the bubble is removed. Cap the bottle and check again for an air bubble. Repeat if necessary.

- If no bubble is present in the sample, create a water seal by adding distilled or deionized water to the top of the BOD bottle around the glass stopper. Then place the overcap over the stopper on the BOD bottle to minimize evaporation from the water seal.

- Place the sealed BOD sample in the air incubator or water bath and incubate the sample at 20°C ± 1°C for 5 days.

- At the end of 5 days ± 4 hours, remove the BOD bottles from the incubator, remove the overcap, pour off the water seal, remove the ground-glass stopper, and measure the final DO concentration

- The DO uptake (from 0 to 5 days) in the dilution water should not be greater than 0.2 mg/L and preferably not more than 0.1 mg/L. Exceeding the 0.2-mg/L criterion could be grounds for rejecting results of the BOD analysis of the environmental sample

- Dilution water of poor quality will cause an oxygen demand and appear as sample BOD. Improve purification or get the dilution water from another source if DO uptake exceeds 0.2 mg/L

Note for Quality Control: 
The BOD5 test can be quite variable. Collect sufficient field and split replicates (10 to 20 percent) to provide an estimate of method variability.