## Calculator
Airflow Requirements - DIFFUSED Aeration |  |  | Airflow - MECHANICAL (SURFACE) Aeration
INPUT |  |  | INPUT
Design F/M Ratio | 10 |  | Design F/M Ratio | 0.4
Design SRT/MCRT/Sludge Age | 5 | days | Design SRT/MCRT/Sludge Age | 5 | days
Avg daily flow in peak month | 1 | MGD | Avg daily flow in peak month | 1 | MGD
Design Avg cBOD concentration | 300 | mg/L or ppm | Design Avg cBOD concentration | 300 | mg/L or ppm
Design Avg TKN / TN / Ammonia-N conc. | 25 | mg/L or ppm | Design Avg TKN / TN / Ammonia-N conc. | 25 | mg/L or ppm
Volume of Aeration Tank | 0.2 | MGal | Volume of Aeration Tank | 0.2 | MGal
Depth of Aeration Tank | 15 | feet | Field Transfer Rate of Aerator as supplied by manufacturer, if known |  | lbs O2 / HP / hr
Time duration of Aeration system in service | 24 | hours | Choose Aerator type, if Field Transfer Rate of Aerator not known | Low Speed Surface Aerator with Draft Tube
No. of blowers employed | 3 |  | Average rated horsepower of aerator | 200 | HP
|  |  | Time duration of Aerators in service | 12 | hours
EQUATIONS |  | SOURCES | No. of aerators in service | 1 | nos.
https://www.sciencedirect.com/topics/engineering/oxygen-requirement
|  | http://courses.washington.edu/onsite/activated%20sludge%20and%20SBR%20pdf.pdf | EQUATIONS |  | SOURCES
https://www.sciencedirect.com/topics/engineering/oxygen-requirement
http://courses.washington.edu/onsite/activated%20sludge%20and%20SBR%20pdf.pdf
https://www.dec.ny.gov/docs/water_pdf/oxcapmech.pdf
i) y = 5(x^2) - 0.5x + 1.2 , where y = O2 for unit cBOD removed (lbs/lb), x = F/M ratio
ii) R = (0.75B + 0.05MV) * 1.5, where R = O2 for cBODl (kg/day), B = cBOD (kg/day)
where M = MLSS (kg/m3), V = Aeration Tank Vol (m3), *for F/M range 0.1 - 1.0 |  |  | i) y = 5(x^2) - 0.5x + 1.2 , where y = O2 for unit cBOD removed (lbs/lb), x = F/M ratio
iii) y = 0.183 * ln (SRT) + 0.7559, where y = O2 for unit cBOD removed (lbs/lb) |  |  | ii) R = (0.75B + 0.05MV) * 1.5, where R = O2 for cBODl (kg/day), B = cBOD (kg/day)
where M = MLSS (kg/m3), V = Aeration Tank Vol (m3), *for F/M range 0.1 - 1.0
OUTPUT |  |  | iii) y = 0.183 * ln (SRT) + 0.7559, where y = O2 for unit cBOD removed (lbs/lb)
O2 required for unit cBOD removal from design F/M ratio | 496.2 | lbs O2/lb cBOD removed | iv) Horsepower = Torque x RPM / 5252
MLSS based on design F/M, Max. monthly flow | 150 | mg/L | v) Standard Field O2 Transfer Rate ranges (in lbs O2 / HP / hr)
Daily O2 required for cBOD removal from design F/M (eq. i) | 1241492 | lbs O2 / day | Low Speed Surface Aerator | 1.15 | 2.1
Daily O2 required for cBOD removal from design F/M (eq. ii) | 2836 | lbs O2 / day | Low Speed Surface Aerator with Draft Tube | 1.15 | 2.3
O2 required for cBOD removal from design SRT/MCRT/SA | 1.1 | lbs O2/lb cBOD removed | High Speed Floating Aerator | 1.15 | 2.1
Daily O2 reqd for cBOD removal from design SRT/MCRT/SA | 2752 | lbs O2 / day
O2 required for Nitrification (option 1) | 4.6 | lbs O2/lb TKN | OUTPUT
O2 required for Nitrification (option 2) x 1.5 (PF) | 4.3 | lbs O2/lb TKN | O2 required for unit cBOD removal from design F/M ratio | 1.8 | lbs O2/lb cBOD removed
Daily O2 required for Nitrification (as per option 1) | 959 | lbs O2 / day | MLSS based on design F/M, Max. monthly flow | 3750 | mg/L
Daily O2 required for Nitrification (as per option 2) | 1345 | lbs O2 / day | Daily O2 required for cBOD removal from design F/M (eq. i) | 4504 | lbs O2 / day
Are both Nitrification & Denitrification mandatory? | YES |  | Daily O2 required for cBOD removal from design F/M (eq. ii) | 3286 | lbs O2 / day
Actual O2 requirement (AOR) from design F/M Ratio | 1242837 | lbs O2 / day | O2 required for cBOD removal from design SRT/MCRT/SA | 1.1 | lbs O2/lb cBOD removed
Actual O2 requirement (AOR) from design SRT/MCRT/SA | 4097 | lbs O2 / day | Daily O2 reqd for cBOD removal from design SRT/MCRT/SA | 2752 | lbs O2 / day
Correction factor for Temp, Pr, etc. | 0.4 |  | O2 required for Nitrification (option 1) | 4.6 | lbs O2/ lb TKN
Standard O2 requirement (SOR) from design F/M Ratio | 3107093 | lbs O2 / day | O2 required for Nitrification (option 2) x 1.5 (PF) | 4.3 | lbs O2/ lb TKN
Standard O2 requirement (SOR) from design SRT/MCRT/SA | 10243 | lbs O2 / day | Daily O2 required for Nitrification (as per option 1) | 959 | lbs O2 / day
Avg O2 transfer efficiency of equipment | 1.5% | per ft. submergence | Daily O2 required for Nitrification (as per option 2) | 1345 | lbs O2 / day
Total Field O2 requirement from design F/M Ratio | 13809302 | lbs O2 / day | Are both Nitrification & Denitrification mandatory? | YES
Total Field O2 requirement from design SRT/MCRT/SA | 45524 | lbs O2 / day | Actual O2 requirement (AOR) from design F/M Ratio | 5849 | lbs O2 / day
Fraction of O2 in Air | 21% |  | Actual O2 requirement (AOR) from design SRT/MCRT/SA | 4097 | lbs O2 / day
Total Air requirement from design F/M Ratio | 65758581 | lbs Air / day | Average Feld transfer rate of selected Aerator configuration | 1.73 | lbs O2 / HP / hr
Total Air requirement from design SRT/MCRT/SA | 216781 | lbs Air / day | Reqd avg HP per aerator (from design F/M Ratio) for given Runtime, Aerators | 282 | HP
Volume occupied by 1 lb of Air at STP | 12.39 | cu ft | Reqd avg HP per aerator (from design SRT/MCRT/SA) for given Runtime, Aerators | 197 | HP
Total Air flow required (from design F/M Ratio) | 565798 | scfm | Reqd avg daily runtime per aerator (from design F/M Ratio) for given HP, Aerators | 17 | hours
Total Air flow required (from design SRT/MCRT/SA) | 1865 | scfm | Reqd avg daily runtime per aerator (from design SRT/MCRT/SA) for given HP, Aerators | 12 | hours
Total Air flow reqd per blower (from design F/M ratio) | 188599 | scfm per blower | Reqd no. of aerators (from design F/M Ratio) for given HP, Runtime | 2 | nos.
Total Air flow reqd per blower (from design SRT/MCRT/SA) | 622 | scfm per blower | Reqd no. of aerators (from design SRT/MCRT/SA) for given HP, Runtime | 1 | nos.
If airflow per diffuser is too high & additional aeration zones are available, put additional aeration zones in service
Recommended Air flow required : 750 to 2000 cu ft/lb BOD removed
Recommended Minimum required airflow/unit length : 3 scfm/lin. ft.
Total cBOD per day | 2502 | lbs/day
Total Air requirement per day (from design F/M Ratio) | 814748819 | cu ft/day
Total Air requirement per day (from design SRT/MCRT/SA) | 2685917 | cu ft/day
Vol. Air required / lb cBOD removed (from design F/M Ratio) | 325639 | cu ft/lb BOD removed
Vol. Air required / lb cBOD removed (from design SRT/MCRT/SA) | 1074 | cu ft/lb BOD removed

## O&M
DIFFUSED AERATION SYSTEM |  |  |  |  | MECHANICAL SURFACE AERATION SYSTEM
| SN | Problem | Observations / Checks | Recommendation |  | SN | Problem | Observation / Check | Recommendation
LOW DO PROBLEMS | 1 | Diffusers need cleaning or repair | 1. Look for signs of poor mixing pattern or uneven surface aeration. Refer "Mixing Criteria" sheet 2. Little to no turbulence 3. Deflocculation 4. Check diffusers for clogging | Check maintenance records for last cleaning of blowers. Bump or chemically clean in-place diffusers if they've not been cleaned for the last 12 months. Take basins out of service and manually clean diffusers. Replace broken diffusers or periodically replace all diffusers if they've gone beyond expected service life. When corrected aerate continuously until brown color and DO return. Then return to time clock operation. | LOW DO PROBLEMS | 1 | Water level too low for mechanical aerator impeller, ie, Inadequate impeller submergence, causing Motor Overload | 1. Noise of the surging of water surface and waves caused by mechanical aeration equipment 2. Check impeller submergence level and compare with manufacturer's recommendation for minimum submergence | 1. Raise or shorten aeration tank weir / Lower impeller. Increase level in basin to provide recommended minimum impeller submergence 2. Repair leaks in weirs or gates that allow water level to drop below desired level during low flows 3. Reduce aeration tankage on-line if otherwise impossible, to raise the water surface. 4. Consider experimenting with baffles, draft tubes, etc. 5. Check the aeration tank weir for leaks. 6. Increase the return rate as a last resort
| 2 | Leaks in air piping. If blowoffs present, air releasing through blowoffs | 1. Check for excessive diffuser headloss or blowoff malfunction. Check air pipe & joints, listen for air leakage or soap test. 2. Watch for bubbling, especially on surface near diffuser header pipe. 3. Generally, little to no turbulence | 1. Check maintenance records for last cleaning of blowers. Bump or chemically clean in-place diffusers if they've not been cleaned for the last 12 months. Take basins out of service and manually clean diffusers. Replace broken diffusers or periodically replace all diffusers if they've gone beyond expected service life. When corrected aerate continuously until brown color and DO return. Then return to time clock operation. 2. Repair Blowoff system. Tighten flange bolts and/or replace flange gaskets |  | 2 | Basin design prone to wave formation at aerator | Visual observation of waves reflecting off surfaces, creating standing waves | Adjust aerator speed or position, if possible or modify basin using baffles to reduce standing wave effect
| 3 | Imbalance with diffuser header valves, improper air distribution | Check airflow to basin. Check valve adjustment | Balance or manually adjust valves as required to better distribute air |  | 3 | Aerator blades / Impeller fouled with rags or debris | 1. Check for vibration, visual observation of impeller, visual observation of splash pattern 2. Check blades for rags or debris | Take aerator out of service and remove rags or debris from impeller
| 4 | Poor blower performance | Check blower - PM required, service record, design & present output | Repair as read |  | 4 | Aerator blades / Impeller fouled with ice | 1. Check for vibration, visual observation of impeller, visual observation of splash pattern 2. Check blades for ice | Take aerator out of service and remove ice from impeller, install manufacturer approved shields that keep splash confined to basin and minimize ice formation
| 5 | Aeration control system needs adjustment | Compare control parameter values to set points | If insufficient air is provided under automatic operation, adjust controls to increase airflow when setpoints are maintained |  | 5 | Aerator speed too low | 1. Check Aerator speed 2. Look for signs of poor mixing. Refer "Mixing Criteria" sheet 3. Little to no turbulence 4. Deflocculation | Refer "Calculator" sheet. Compare pollutant loadings to design values. Increase Aerator speed accordingly.
| 6 | Dirty inlet air | Check inlet air pressure between filter and blower | Replace inlet filters. Clean filters if washable |  | 6 | Too few aerators in operation / low runtime / inadequate power rating | 1. Check number of aerators in operation. 2. Look for signs of poor mixing. Refer "Mixing Criteria" sheet 3. Little to no turbulence 4. Deflocculation | Refer "Calculator" sheet. Compare pollutant loadings to design values. Increase the no. of aerators in operation, runtime or motors with higher power rating as required.
| 7 | Blower malfunction | Compare airflow at each blower to its performance curve(s) | Diagnose and repair/replace malfunctioning parts. Check setting of inlet air vanes/valves |  | 7 | Difficult to maintain DO at head end due to improper Organic Load distribution to tanks | Check DO profile through the process | If possible, change influent points from plug flow to step feed or complete mix
| 8 | Equipment not operating (check time clock first, may not be on “off” cycle) | Air bubbles rising, chocolate color, little or no foam, 20-30% solids, DO no more than 1 ppm or 1 mg/L | Check for power outage, fuses blown-replace. Reset circuit breaker. Motor overloaded-push reset button. Check overload heaters if reset button does not start motor. Check “V” belt drive. | HIGH DO PROBLEMS | 8 | Over-Aeration resulting in high DO | 1. Boiling action, violent or excessive turbulence or splashing throughout Aeration Tank. Large bubbles more than 0.5 in. in diameter 2. Check DO throughout the process, recommended in range of 1.0-3.0 mg/L throughout 3. Compare pollutant loadings to design values | 1. Lower or lengthen aeration tank weir / Raise impeller. Decrease level in basin to provide recommended maximum impeller submergence at peak flow 2. Increase aeration tankage on-line if otherwise impossible, to raise the water surface. 3. If aerators allow, periodically reduce the speed of aerator to reduce oxygen transfer but maintain mixing 4. Consider experimenting with baffles, draft tubes, etc. 5. If DO is still too high, take aerator out of service, use low speed, if two- speed aerators, or take an aeration zone out of service to maintain minimum impeller submergence 6. If aerators allow, periodically reduce the speed of aerator to reduce oxygen transfer but maintain mixing 7. If aerator is able to re-suspend solids, consider shutting off aerator(s) (not more than 1.5-2 hrs off to prevent odors). Use a combination of on time and either reduced speed time or off time throughout the day to better match aeration to the oxygen demand. For large aerators, on-off operation may be too hard on gear reducers; consider soft-start of motors if on-off operation is used. 8. Decrease the return rate as a last resort
| 9 | Rising air bubbles despite equipment in good operation | Air bubbles rising. Light muddy color, too much foam, 5- 10% solids, murky supernatant, poor separation of liquid and solids. | Plant is running too much. Reduce running time to minimum necessary to maintain brown color. Common during start-up period. Use commercial de-foamer if necessary. |  | 9 | Too much DO in internal recycle suction, causing high DO in Anoxic zones | 1. Check DO in Aeration Zone where internal recycle starts 2. Boiling action, violent or excessive turbulence or splashing throughout Aeration Tank. Large bubbles more than 0.5 in. in diameter | 1. For activated sludge process with internal recycle, DO profile can be tapered for low DO at internal recycle suction. Adjust submergence 2. Adjust basin levels, use baffles and/or modify inlet ports to minimize turbulence and introduction of DO to anoxic zones
| 10 | Equipment will work on manual but not automatic. | Equipment will work on manual but not automatic. | Possible failure of time clock, have electrician check. Overload may be released - push reset button. |  | 10 | Too much turbulence at influent, causign significant DO and/or NO2+NO3-N in Fermentation Zones | Boiling action, violent or excessive turbulence or splashing throughout Aeration Tank. Large bubbles more than 0.5 in. in diameter | Adjust basin levels, use baffles and/or modify inlet ports to minimize turbulence and introduction of DO to anoxic zones
| 11 | All equipment operating properly except spray systems. | Excessive foam | Possible spray pump not operating-check power supply and push reset. Possible pump plugged- remove pump and clean intake. Possible clogged nozzles- clean. |  | 11 | Water level too high for mechanical aerator impeller, causing Motor overload | Check impeller submergence level, especially at peak flow | 1. Lower or lengthen aeration tank weir / Raise impeller. Decrease level in basin to provide recommended maximum impeller submergence at peak flow 2. Increase aeration tankage on-line if otherwise impossible, to raise the water surface.
| 12 | Too few blowers in operation | 1. Check number of blowers in operation and control system 2. Look for signs of poor mixing pattern or uneven surface aeration. Refer "Mixing Criteria" sheet 3. Little to no turbulence 4. Deflocculation | Refer "Calculator" sheet. Compare pollutant loadings to design values. Increase the no. of blowers in operation or adjust controls to bring on more blowers if automatically controlled
| 13 | Air flow too low for proper observation of blowers | 1. Compare airflow divided by no. of diffusers to acceptable low value, for your organic loading. Roughly 750 to 2000 cu ft of air required per lb BOD removed. 2. Look for signs of poor mixing pattern or uneven surface aeration. Refer "Mixing Criteria" sheet 3. Little to no turbulence 4. Shearing of flocs | Refer "Calculator" sheet. Compare pollutant loadings to design values. Increase airflow to provide at least minimum recommended airflow per diffuser. Increase until DO is between 1.0-3.0 mg/L in Aeration Zones. |  | DETAILED CHECKS : Routine preventive maintenance by emptying Aeration Tanks necessary for A. Performing detailed inspection of the structure, valves, and control gates B. Cleaning out grit and settled solids C. Maintaining equipment and piping
| 14 | Difficult to maintain DO at head end due to improper Organic Load distribution to tanks | Check DO profile through the process | If possible, change influent points from plug flow to step feed or complete mix |  | SN | Unit |  | Checks for Maintenance
| 15 | Difficult to maintain DO at head end due to improper Air distribution to tanks | Check Air distribution | If possible, redistribute the air. If necessary, consider changing diffuser layout |  | 1 | General | 1. Use gloves when examining your aerator motor. Wash hands immediately after any maintenance is completed. 2. Always turn power off at the breaker before removing the motor for inspection or service. 3. Children and pets should be kept away from the system discharge area. | A. Consult the O&M manual for the lubrication needs of the motor, gear box, shaft, and others B. Inspect aerators C. Check for unusual vibration
HIGH DO PROBLEMS | 16 | Over-Aeration resulting in high DO | 1. Boiling action, violent or excessive turbulence or splashing throughout Aeration Tank. Large bubbles more than 0.5 in. in diameter 2. Check DO throughout the process, recommended in range of 1.0-3.0 mg/L throughout 3. Compare pollutant loadings to design values | Refer "Calculator" sheet. Decrease airflow to provide, at most, the maximum recommended airflow per diffuser. If diffusers allow, reduce the amount of air added by periodically reducing or shutting off air (not more than 1.5 - 2 hrs off to prevent odors). Use a combination of on time and either reduced airflow time or off time throughout the day to better match aeration to the oxygen demand |  | 2 | Aeration Tank |  | Have your tank pumped out at least every 4 years by a registered hauler, more frequently if needed.
| 17 | Air rate too high for proper operation of diffusers | Compare airflow divided by number of diffusers to acceptable high value | Refer "Calculator" sheet. Decrease airflow to provide, at most, the maximum recommended airflow per diffuser. If diffusers allow, reduce the amount of air added by periodically reducing or shutting off air (not more than 1.5 - 2 hrs off to prevent odors). Use a combination of on time and either reduced airflow time or off time throughout the day to better match aeration to the oxygen demand |  | 3 | Motor |  | Recommended that a service contract for routine maintenance and service be obtained from the local manufacturer’s representative.
| 18 | Too many blowers in operation | 1. Boiling action, violent or excessive turbulence or splashing throughout Aeration Tank. Large bubbles more than 0.5 in. in diameter 2. Check DO throughout the process, recommended in range of 1.0-3.0 mg/L throughout 3. Compare pollutant loadings to design values | Refer "Calculator" sheet. Decrease airflow to provide, at most, the maximum recommended airflow per diffuser. If diffusers allow, reduce the amount of air added by periodically reducing or shutting off air (not more than 1.5 - 2 hrs off to prevent odors). Use a combination of on time and either reduced airflow time or off time throughout the day to better match aeration to the oxygen demand |  |  | Motor Operation |  | Check your motor and timer routinely. Listen for the sound of the motor running. It is now recommended to run aeration motors continuously. If run on a timer, it should run no less than 30 minutes of every hour. A manufacturer’s representative can set the timer to the proper operating cycle. When the motor is off for long periods of time, it cools and allows condensation to enter the motor housing and potentially shorten the motor life.
| 19 | Aeration control system needs adjustment | Compare control parameter values to setpoint(s) | If excess air is provided under automatic operation, adjust controls to decrease airflow when setpoints are maintained |  |  | Motor Shaft |  | To inspect or clean the motor shaft, turn power off at the breaker, unplug the motor and lift it straight up to examine the aspirator shaft. Use care so the shaft is not bumped or bent. The stainless shaft and nozzle-like aspirator should be straight, free of hair, lint, and any debris. An aspirator nozzle is attached to the shaft bottom to provide air input and circulation as the motor rotates the shaft. Cleaning the shaft monthly will reduce stress placed on the motor and will help increase motor longevity.
| 20 | Too much DO in internal recycle suction, causing high DO in Anoxic zones | 1. Check DO in Aeration Zone where internal recycle starts 2. Boiling action, violent or excessive turbulence or splashing throughout Aeration Tank. Large bubbles more than 0.5 in. in diameter | 1. For activated sludge process with internal recycle, DO profile can be tapered for low DO at internal recycle suction. Adjust submergence 2. Adjust basin levels, use baffles and/or modify inlet ports to minimize turbulence and introduction of DO to anoxic zones |  |  | Air Intake |  | While the motor is running and with gloves on, place a finger on the top of the air intake tube (refer Image MOT1). You should feel suction. If there is no suction, unplug and remove the motor to check for debris inside the motor or the shaft. The shaft can be cleared by removing and cleaning the aspirator (right-hand thread) and using a water hose or a long rod to clear obstructions. If required, the shaft can be removed by loosening the 2 lowest Allen screws below the motor housing to make removing debris easier. If no debris or blockage is found, and there is still no suction, the motor may need service. If your motor has an air filter, ensure that it's cleaned or replaced periodically. Check that hose connections are secure and verify that air is reaching the tank when the pump is running
| 21 | Too much turbulence at influent, causign significant DO and/or NO2+NO3-N in Fermentation Zones | Boiling action, violent or excessive turbulence or splashing throughout Aeration Tank. Large bubbles more than 0.5 in. in diameter | Adjust basin levels, use baffles and/or modify inlet ports to minimize turbulence and introduction of DO to anoxic zones |  | 4 | Filters |  | Pumping and cleaning a Jet up flow filter (a large, rectangular lid, if present) is recommended every six months. Rake the gravel while hosing down the filter with a hose to break up accumulated biological growth. This liquid should be pumped back into the aeration tank. Locate and clean the nylon mesh filter, if present (it might be located in the third compartment) on a regular basis by licensed service personnel.
[6 empty] | 5 | Chlorination |  | If present, tablets should be placed in the tubes periodically. Use only calcium hypochlorite tablets designed for sewage treatment, not pool chlorine tablets.
| DETAILED CHECKS : Routine preventive maintenance by emptying Aeration Tanks necessary for A. Performing detailed inspection of the structure, valves, and control gates B. Cleaning out grit and settled solids C. Maintaining equipment and piping |  |  |  |  | 6 | Risers |  | All compartments should have watertight risers properly installed above the ground surface to prevent soil and surface water from entering the system. Risers will allow your system to be easily accessed for service and inspections. Your system will have to be pumped more frequently if soil is allowed to enter. Soil influx can damage the aerator motor, clog the filter, or even create a blockage in the effluent line.
| SN | Unit |  | Checks for Maintenance |  | 7 | Access |  | Any shrubbery and/or vegetation around the aerobic system must be maintained to accommodate routine system maintenance and inspection.
| 1 | Aeration Tank |  | Have your tank pumped out at least every 4 years by a registered hauler, more frequently if needed. PRECAUTIONS: 1. Use gloves when examining your aerator motor. Wash hands immediately after any maintenance is completed. 2. Always turn power off at the breaker before removing the motor for inspection or service. 3. Children and pets should be kept away from the system discharge area. |  | 8 | Discharge |  | 1. Aerobic systems that discharge to surface water drainage must have outlets that are accessible for inspection. The outlet pipe needs to flow freely. Ideally, there should be 6 inches between the bottom of the discharge pipe and the receiving waterway. The receiving waterway should be maintained so that discharged water keeps moving away. 2. Aerobic systems with leaching typically have two sets of leach lines. A square (sometimes round, plastic) distribution box provides switching between each set of leach lines using a PVC 90° elbow (or a paddle on plastic risers). The elbow should be switched every six months. This allows one set of leach lines to rest while the other accepts the system effluent.
| 2 | Centrifugal Blowers |  | 1. Unusual noise or vibrations 2. Lubrication of blowers and motors 3. Check and lubricate couplings 4. Check discharge pressure and temperature 5. Check filters and obstructions 6. Check amperage meter
| 3 | Postive Displacement Blowers |  | 1. Unusual noise or vibrations 2. Lubrication of blowers and motors 3. Check and lubricate couplings 4. Check and exercise pressure relief valve 5. Check discharge pressure and temperature 6. Check filters and obstructions 7. Check blower seals 8. Check drive belt alignment and tension
| 4 | Coarse Bubble Diffusers |  | 1. Aeration basins should be drained annually 2. Remove excess settled solids that have accumulated 3. Clean diffusers and piping assemblies as needed 4. Inspect all hardware and components 5. Repair, replace, and tighten components as needed 6. Refill aeration tank following startup procedures
| 5 | Fine Bubble Diffusers |  | 1. Aeration basins should be drained annually 2. Drain aeration basin and leave air on 3. Remove excess settled solids that have accumulated 4. With air on, hose off and wash each diffuser with clean water 5. With air off, if needed scrub each diffuser with either a soft bristle brush or rag 6. Turn air back on and repeat hosing procedure for each diffuser 7. Inspect all hardware and components 8. Repair, replace, or tighten components as needed 9. Refill aeration tank following startup procedures

## Mixing Criteria
SN | PARAMETER | INCOMPLETE MIXING - Indicators / Design Characteristics | THOROUGH MIXING - Indicators / Design Characteristics
1 | Reactor Shape | 1. Very long length to width ratio (greater than 4:1) with inlet at one end (width side) and outlet at opposite end. | 1. Circular Tank - No criteria, or
|  | 2. System is designed or operated with biomass separation within the aeration system. | 2. Rectangular Tank - Small length/width ratio (3:1 or less).
2 | Mixing | 1. Entering recycled biomass and wastewater are not quickly dispersed. Indications of poor dispersion may be: | 1. Unit does not have baffles or partitions.
|  | - visual indication of solids settling | 2. Jet aeration system - Pumping rate should be > 5 times the entering wastewater and recycle flow rate.
|  | - plume with visual differences in color or solids level | 3. Diffused system air flow rate > 10 scfm/1000 cu. ft.
2. The unit has baffles or partitions within the tank, or aeration units are operated in series.
3. Mixing does not occur between inlet and outlet.
3 | Aeration Equipment | 1. Rolling or tapered aeration | 1. Diffused aeration - Well operated (unplugged) subsurface fine bubble diffused (Porous Diffusers) system such as plate, dome, disc, tube. Depth : 15 ft minimum. Location : Full Floor Coverage (indicated by uniform bubble distribution on surface of basin)
|  | 2. Aerators (submerged or surface aerators) located such that there are zones that are not mixed (i.e., relatively stagnant or dead zones) | 2. Jet aeration system - per manufacturers criteria, with subsurface flow only. Depth : used in deep tanks (25 ft or greater). Location : Liquid pumping with air diffusion occurs at bottom of tank.
3. Significant distance between aeration equipment such that solids settling results
4 | Inlet | 1. Wastewater inlet is located relative to the surface aerator such that the entering wastewater is exposed to the air before significant mixing. | 1. Multiple inlet points or inlet located near point of significant mixing.
|  | 2. Inlet located such that wastewater enters the unit at a relatively stagnant zone. | 2. Submerged inlet
3. Inlet located above the surface, at the surface, or near the surface.
5 | Effluent Outlet | Located such that short circuiting occurs between inlet and outlet. | Located such that short circuiting does not occur between inlet and outlet.
| SOURCE : | "Technical Support Document for Evaluation of Thoroughly Mixed Biological Treatment Units" - EPA
https://www3.epa.gov/ttn/atw/nsps/socww/mulmix5.pdf
1. A thoroughly mixed treatment unit is a unit that is designed and operated to approach or achieve uniform biomass distribution and organic compound concentration throughout the aeration unit by quickly dispersing the recycled biomass and the wastewater entering the unit.
2. The EPA=s intent is that this definition reflect the modeling that was used, in part, as the basis for the decision (1) to exempt certain systems treating list 1 compounds from the requirement to determine the fraction biodegraded (Fbio) and (2) to allow the easier procedures for determining Fbio for systems meeting the definition but treating list 1 and 2 compounds.
3. IMPORTANT FEATURES : biomass is recycled, the biomass approaches or achieves a state of being suspended uniformly throughout each aeration unit the biomass concentration is not less than 1 kilogram/cubic meter, and that influent materials are rapidly dispersed throughout the unit. key design criteria for ensuring that the list 1 compounds are efficiently biodegraded in the biological treatment unit prior to the opportunity for significant volatilization to the atmosphere
4. Consequently, the criteria and procedures provided in this document for determining whether a biological treatment unit can be considered a “thoroughly mixed treatment unit” are based on evaluating the rate of mixing relative to the rate of stripping or volatilization.
5. Practically, small insignificant Dead/Stagnant zones are expected, but there is enough mixing to support suspension, so no accumulation on sides or floor.
6. INSUFFICIENT MIX => BIOMASS Accumulates on floor - SIGNS : Biomass layers, Low DO, Anaerobic decay at base of floor, less Biomass generation than is theoretically expected.

## STATS
DO Requirements | SYSTEM | Air per BOD | Air per Lin feet | DO reqd. | SOTE | SOTR (lbs O2/hp hr) | AOTR (lbs O2/hp hr)
1. Each bug needs 0.1-0.3 mg/L | Diffused Aeration | Min 750 to 2000 cu ft/lb BOD removed | Min. 3 scfm/lin. ft. |  | 10-40% in clean water at 15 ft submergence COARSE : 9-13% FINE : 13-40% |  | COARSE : 1 - 2 FINE : 1.3 - 2.5 | COARSE : 0.2-0.5 in. dia FINE : 0.04-0.1 in. dia
2. if <2 mg/L then bugs outside floc consume. Bugs inside die, floc breaks |  |  |  |  | COARSE: <1% /ft submg
3. F/M 1 => DO 5 mg/L |  |  |  |  | JET : 1-2% / ft submg
4. Often F/M <= 0.5 => DO 2 mg/L fine, but if F/M > 0.4 => DO 4 mg/L |  |  |  |  | FINE : 2% / ft submg
BOD removal max at 1, NITF max at 2...but DO needs to reach flocs | Surface Aeration |  |  | 1.0 - 1.5 lbs O2 per lb BOD removed |  |  | 1.8 - 2.5 lbs O2/ hp hr
5. At High F/M, high OUR => MLSS inc helps remove low DO filaments. Inc DO also concurrently. RAS inc also
6. Common experience - takes higher DO to control low DO bulk than to prevent it. Chlorintn also short term option
7. Step feeding of wastes helps solve low DO blk, but can lead to low F/M blk
8. Higher aeration causes more foam due to physical action of more air present. Inc DO can also lead to DN problem.
Recommended range : 1.0 - 3.0 mg/L
Oxygen Requirement in Theory
per lb COD : 0.9 - 1.3 lbs O2
per lb TKN : 4.57 lbs O2
if all of the cells can be oxidized completely, the ultimate BOD of the cells is equal to 1.42 times the concentration of cells.
The air demand, given in terms of standard cubic feet per minute (scfm), is calculated by accounting for the specific weight of air at standard temperature, as well as the mass fraction of oxygen in air.
Additionally, the Standard Oxygen Transfer Efficiency (SOTE) of the aeration equipment must be applied to the air demand calculation
Air demand calculations must also account for the quantity of air required to maintain biomass in suspension.
The volume of air required to provide sufficient mixing depends on a variety of factors, including the tank geometry and the biomass concentration
The tank geometry is a key factor to consider because typically the back of the aeration tank receives a limited amount of mixing, especially if a tapered grid system is utilized
In suspended growth aeration systems, the air demand for mixing is typically less than that required for oxygen transfer to support biological processes.
In fixed growth and Integrated Fixed-Film Activated Sludge (IFAS) biological processes, mixing requirements often exceed process aeration requirements due to the fixed or floating media added to the Mixed Liquor Suspended Solids (MLSS) that promotes additional biological growth. However, the air demand requirements for mixing should still be compared with the air demands for oxygen transfer across all of the zones of an aeration tank to ensure that sufficient mixing air is provided.

## Equipment Issues
Blower Maintenance Whether centrifugal or positive displacement, blowers are difficult and expensive to repair, largely due to the fact that they operate at high speed and are machined to very close tolerance. Wastewater treatment plant shops are seldom equipped to perform major repairs on this type of equipment, and usually contract for this work to be done. Heat, vibration, and dust are often causes of premature wear and blower failure. Improperly maintained air filters which results in suction side air restrictions, or leaks which allow dust to enter the blower are damaging to either type of blower. Lubrication and other preventive maintenance must be done in accordance with the manufacturer’s specifications.
Piping Piping which connects the blower to the air diffusion system at the aeration tank may be either a simple drop pipe extending from the deck of the aeration tank to the floor of the tank, or may be a swing type system. The advantage of the swing system is that hinges in the piping allow the operator to retrieve a bank of aerators out of the tank using a crane on the deck of the tank when diffuser maintenance is needed. Needless to say, this operation requires an adequate crew and careful observance of all safety considerations.
The most efficient system is a combination of fine bubble diffusers, full floor coverage, diffuser placement, and an annual cleaning requirement.
A coarse bubble system placed in full floor coverage has low maintenance requirements but OTE is approximately half of a fine bubble diffuser.
A fine bubble diffuser system used in non-full floor coverage placement (side roll or center roll) is not any more efficient than a typical coarse bubble diffuser, but may require more maintenance than the coarse bubble diffuser.
SIDE ROLL, MID ROLL, DUAL MID ROLL, FULL FLOOR COVERAGE Configurations, in increasing order of Efficiency
The most efficient aeration system is a combination of fine bubble and high OTE with the diffusers placed in full floor coverage with a mid-range system pressure (6 to 8 psi) and annual cleaning. A coarse bubble diffuser system placed in full floor coverage has low maintenance requirements but a much lower OTE (about half of fine bubble diffusers). Fine bubble diffusers used in a side roll or center roll placement are not any more efficient than a similarly placed coarse bubble diffuser and may require more maintenance.
All maintenance and repairs should be documented. Consult the O&M manual for all maintenance needs.
WRRFs may also draw foul air from the headspace of process tanks or from odorous buildings such as preliminary treatment facilities for odor control, and use that air for aeration of biological processes. Odorous air, however, contains compounds that could potentially lead to corrosion of aeration equipment, and if odorous air is used for aeration, careful consideration for compatible materials must be included in the selection and design of aeration equipment.
List the maintenance considerations for a mechanical aeration system. A. Consult the O&M manual for the lubrication needs of the motor, gear box, shaft, and others B. Inspect aerators C. Check for unusual vibration All maintenance and repairs should be documented.
2.4.3 List the maintenance considerations for diffusers. A. Check surface aeration patterns for uneven distribution B. Check air line pressure reading C. Check and purge moisture as needed D. Drain, inspect, and clean the aeration tanks annually All maintenance and repairs should be documented. Consult the O&M manual for additional maintenance needs.
2.4.4 Compare the maintenance requirements of fine bubble to coarse bubble diffuser systems.
A. Course bubble aeration systems 1. Aeration basins should be drained annually 2. Remove excess settled solids that have accumulated 3. Clean diffusers and piping assemblies as needed 4. Inspect all hardware and components 5. Repair, replace, and tighten components as needed 6. Refill aeration tank following startup procedures B. Fine bubble aeration systems 1. Aeration basins should be drained annually 2. Drain aeration basin and leave air on 3. Remove excess settled solids that have accumulated 4. With air on, hose off and wash each diffuser with clean water 5. With air off, if needed scrub each diffuser with either a soft bristle brush or rag 6. Turn air back on and repeat hosing procedure for each diffuser 7. Inspect all hardware and components 8. Repair, replace, or tighten components as needed 9. Refill aeration tank following startup procedures
2.4.5 Discuss the importance of routine preventative maintenance of aeration basins and clarifiers. Aeration basins and clarifiers should be emptied on a regular basis to: A. Perform a detailed inspection of the structure, valves, and control gates B. Clean out grit and settled solids C. Maintain equipment and piping

## Process Control
DO CONTROL METHODS
DIFFUSED AERATION | SURFACE AERATION
Controlling air valves | Increasing or decreasing the aerator speed by using VFDs
Controlling the blower output such as using variable frequency drives (VFD) | Increasing or decreasing the aerator submergence by adjusting the tank water level
Increasing or decreasing the number of blowers in operation | Increasing or decreasing the number of aerators in operation
Cleaning or replacing diffusers | Process control (ex: MLSS levels)
Changing the number of diffusers
Process control (ex: MLSS levels)
[NOTE: Throttling air valves with a positive displacement blower will not reduce air flow output but will raise operating pressure of the blower with high electric cost as the result. Throttling an inlet air valve on a centrifugal blower will reduce air discharge flow.]

## Monitoring
Sampling and in-line testing of various pollutants of interest (such as pH, ammonia, orthophosphorus, etc) allows for a rapid assessment of the treatment occuring in various stages of the plant and troubleshooting any treatment problems or variability. Pacing blower output from in-line aeration basin DO sensors provides for greater energy efficiency by deliveringoxygenbasedontheincomingwasteload. RASflowratescanbeadjusted based on influent flow rates to help maintain a more consistent sludge blanket in the clarifiers and more consistant MLSS concentrations in the aeration basin. The use of and placement of in-line monitoring probes and sensors is dependent upon treatment objectives.
A. Dissolved oxygen (DO) meter
A DO meter is used to monitor aeration basin dissolved oxygen levels. Many plants have in-line DO sensors to automatically control DO levels. If manual measurements are made, they should be taken in each aeration basin using a field DO probe.
FACTORS AFFECTING DO
An increase in influent BOD (food) will increase oxygen demand and more aeration may be required to treat the incoming BOD
An increase in wastewater temperature lowers the solubility of oxygen in water thus requiring more air. This usually happens during summer operations.
A loss of viable bacteria in the aeration basin may result in higher than normal DO because dead bacteria will be unable to consume the oxygen supplied. The source of the toxicity should be identified and eliminated and the mixed liquor may need to be wasted from the planttoremovethedeadbacteria. Seedingmaybenecessary.
The effluent end of the aeration tank should have a dissolved oxygen level of at least 1.0 mg/L. DO in the aeration tank should be checked every two hours until a pattern is established.