## ConceptFAQs
ABOUT SRT / MCRT / SLUDGE AGE | TYPICAL VALUES
What is it? : | The optimum centerline range of SRT depends on your facility’s design considerations and regulatory compliance requirements.
The terms Sludge Age, SRT, MCRT are terms used to describe the amount of time, in days, that solids or microorganisms are maintained in the activated sludge process before getting wasted. The terms SRT and MCRT vary slightly in definition, while “Sluge Age” can be used to refer to either of these two. | Following are the desirable ranges of SRT that you can aim for based on the treatment process, outcome, conditions, or constraints :
Sludge Age is obtained by dividing the mass of total suspended solids (TSS) in the treatment system by the mass of TSS lost and removed from the treatment system through wasting from the Secondary Clarifier. | Conventional Activated Sludge Process : 5 - 15 days
SRT or Sludge Residence Time measures only the mass of TSS in the Aeration Basin or MLSS. | BOD removal : 3 - 5 days (Summer: 4 days, Winter: < 8 days)
MCRT or Mean Cell Residence TIme measures the mass of TSS in the Aeration Basin (MLSS) and that in the Secondary Clarifier | Provide complete nitrification : 3 - 18 days (Summer: 10 days, Winter < 15 days)
Biological phosphorus removal : 2 - 4 days
How does it work? : | Stabilization of activated sludge : 20 - 40 days
Sludge Age impacts the MLSS concentration in the Aeration Basin. | Minimize sludge production : 30 days
Long sludge age (or Old Sludge) increases the MLSS concentration. | Minimize filamentous bacteria : 15 - 20 days
Short sludge age (or Young Sludge) decreases the MLSS concentration. | Degradation of xenobiotic (toxic) compounds : 5 - 50 days
Why does it matter? :
Since the MLSS concentration is affected by the Sludge Age/SRT/MCRT, it becomes a critical process control number to determine the M in the F/M ratio and keep it in the centerline range.
Maintaining optimal Sludge Age is also necessary to develop good floc and avoid foaming and/or bulking problems.
Where do I control it?
At every WAS line
How do I control it?
If the F/M ratio is too high or MLSS too low - Decrease Sludge Wasting or WAS from the Secondary Clarifier to increase Sludge Age, which increases the M to restore the F/M ratio.
If the F/M ratio is too low or MLSS too high - Increase Sludge Wasting or WAS from the Secondary Clarifier to decrease Sludge Age, which decreases the M to restore the F/M ratio.
Where do I measure it?
At every Aeration Basin and/or Secondary Clarifier
How do I measure it?
You’ll need the following data:
1. MLSS concentration (which refers to TSS in both Aeration Basin (AB) and Secondary Clarifier (SC))
2. Volume (in gallons) of your Aeration Basin (AB)
3. Volume (in gallons) of your Secondary Clarifier (SC), only required for MCRT
4. WAS Flow rate
5. TSS concentration in WAS
6. Flow rate of Secondary Clarifier (SC) effluent
7. TSS concentration in Secondary Clarifier (SC) effluent

## Calculator
CALCULATION TOOL
Target Sludge Age
Maximum Specific Growth corrected for Temperature : μ(max,T)
μ(max,T) = 0.65 x (1.055)^(T-25)
Decay Rate corrected for Temperature, k(d)
k(d) = 0.05 x (1.055)^(T-25)
Growth Rate correction factor for effluent Ammonia : CF(NH4+)
k(N) = 1.0 x (1.055)^(T-25)
CF(NH4) = Effluent Ammonia / ( k(N) + Effluent Ammonia)
Growth Rate correction factor for Dissolved Oxygen : CF(DO)
CF(DO) = DO / (1 + DO)
Growth Rate corrected for Temperature, Ammonia, DO : μ(T)
μ(T) = μ(max,T) x CF(NH4+) x CF(DO)
MCRT = 1 / ( μ(T) - k(d) )
INPUT :
Temperature of Mixed Liquor | 80 | °F
Target TKN in Secondary Clarifier effluent (for Nutrient removal only) | 1 | mg/L
DO in Mixed Liquor | 2 | mg/L
OUTPUT :
Temperature of Mixed Liquor (deg. C) | 26.7 | °C
| Lower Limit | Upper Limit
MCRT (for No Nutrient removal) | 2 | 3 | days
MCRT (for Nutrient removal) | 5 | 6 | days
Current Sludge Age based on Solids Inventory
INPUT :
Note : If your Secondary Clarifier is designed to have a sludge blanket, please use MCRT instead of SRT
Select SRT or MCRT | MCRT
Average MLSS in Aeration Tank(s) | 3500 | mg/L
Net Volume of Aeration Tank(s) | 0.5 | Mgal
Net Volume of Secondary Clarifier(s) | 0.3 | Mgal
Average TSS concentration in Secondary Clarifier Effluent | 20 | mg/L
Average Effluent Flow rate from Secondary Clarifier(s) | 0.2 | MGD
Average TSS concentration in WAS | 8000 | mg/L
WAS Flow Rate | 95000 | gal/day
OUTPUT :
Total Solids in Aeration Tank | 14595 | lbs
Total Solids in Aeration Tank & Secondary Clarifier | 23352 | lbs
Total Solids leaving Activated Sludge Process | 6372 | lbs
| Lower Limit | Upper Limit
MCRT | 5 | 6 | days
Is your facility mandated to remove nutrients? | YES
Your MCRT is within the required range. Don't alter WAS. | R2.3B
Sampling Point | Result | Condition | Code
D : Aeration Basin - Outlend end | Very Low SRT/MCRT | Actual SRT/MCRT < 50% of Design/Target SRT/MCRT | R2.1D
D : Aeration Basin - Outlend end | Low SRT/MCRT | 50% of Design/Target SRT/MCRT < Actual SRT/MCRT < 90% of Design/Target SRT/MCRT | R2.2D
D : Aeration Basin - Outlend end | Normal SRT/MCRT (within 10% of target) | 90% of Design/Target < Actual SRT/MCRT < 110% of Design/Target | R2.3D
D : Aeration Basin - Outlend end | High SRT/MCRT | 110% of Design/Target SRT/MCRT < Actual SRT/MCRT < 150% of Design/Target SRT/MCRT | R2.4D
D : Aeration Basin - Outlend end | Very High SRT/MCRT | 150% of Design/Target SRT/MCRT < Actual SRT/MCRT | R2.5D