## ConceptFAQs
Denitrification is the process whereby nitrogen is removed from water. When employed in water quality improvement technologies, denitrification treats water to reduce its nitrate-nitrogen content to potable levels.
Both nitrification and denitrification are important to biological wastewater treatment. In the nitrification step of the cycle, ammonia oxidizes into nitrites (NO2) and nitrates (NO3). The NO2 and/or NO3 then transform into nitric oxide (NO) and nitrous oxide (N2O), which finally transform into gaseous nitrogen (N2), which is fit for harmless discharge into the atmosphere.
However, the N2 bubbles carry floc upwards (ashing / clumping) causing solids to wash out through weirs, instead of settling down to form concentrated sludge. As a result, the effluent quality is affected and solids are lost from the system.

## Best Industry Practices
Best Industry Practices (Typical values)
1. Secondary Clarifier Retention Time: 2 to 4.5 hours
2. Sludge Blanket Depth: 1 to 3 ft. (No more than 25% of clarifier depth)
3. Regular rotating speed of rake arm or scraper: 1 to 2 rotations per hour.

## Indicators
SIGNS of Denitrification at Secondary Clarifier
1 | Bubbles behind rake arm, scum baffles, near clarifier edges, during peak loading
2 | Popping sound of bubbles when hosed down
3 | Clumping (irregular sized floating solids or flocs)
4 | Ashing (pin flocs) - beginning of Denitrification
5 | Foam/ light scum difficult to control (transition phase)
6 | Pop-ups - light brown to brown, No odor when hosed down or broken with cleaning brush
7 | Sludge falls under scum baffle, then rises

## Monitoring
Monitoring
1 | Look out for visual signs of denitrification at secondary clarifier.
2 | Perform Column settling tests or settleometer test. Stir gently and see if bubbles are released. Samples will show most or all sludge floating to the top within 4 hours.
3 | Check readings on ORP meter. Readings : -75 to -100 mV, Zero DO.
4 | Monitor throughout for Ammonia, Nitrate, Nitrate.
5 | Denitrification occurs within pH range : 7.0-8.5, Temp. : 5 - 30 deg.C
6 | RAS - pH and Alkalinity show drastic increase in the event of denitrification.