## Lab Parameters
SN | Parameter | Holding/Sampling | Pre-Treatment | Apparatus | Procedure | Notes | Calculation |  | Comments
1 | BOD (mg/L) | 24 hrs, Refrigerate at 4°C, Grab/Composite | Temp. 20°C, pH 6.4 to 7.5, dechlorinate the sample | 300 mL BOD incubation bottles, Incubator at 20°C | 5 days in the dark at 20°C | Dilution water depletion < 0.2 mg/L | (DO initial - DO final) x (Bottle Vol/ Sample Vol) | Go to tool | DO depletion in sample bottles must be atleast 2 mg/L, Final DO must be atleast 1 mg/L
2 | TSS (mg/L) | 7 days, Refrigerate at 4°C, Grab/Composite | Well mixed sample | Glass fiber filter (Whatman 934 AM, Millipore AP40, Gelman A/E) | Dry in oven at 105°C ± 2°C until constant weight achieved. | Insert filter paper wrinkled side up | (Wt. of Filter+Sample - Wt. of Filter) x (1/ Sample Vol) | Go to tool
3 | Settleable Solids (mL/L) | 48 hrs, Refrigerate at 4°C, Grab |  | Imhoff cone | Settle for 45 mins, stir gently, settle for 15 mins longer |  | Direct Read
4 | Faecal Coliform (Colonies / 100 mL) | 30 hrs, Refrigerate at 4°C, Grab | Dechlorinate if necessary | Filter paper, Filter funnel, Nutrient broth, Culture dishes, Incubator | Incubate at 35°C ± 0.5°C for 22-24 hrs | 20-60 colony range desired | Colonies counted x 100 x (1/ Sample Vol in mL) | Go to tool
5 | E. coli (Colonies / 100 mL) | 30 hrs, Refrigerate at 4°C, Grab | Dechlorinate if necessary | Filter paper, Filter funnel, Nutrient broth, Culture dishes, Incubator | Incubate at 35°C for 2 hrs, then at 44.5°C for 22 hrs ± 2 hrs | 20-80 colony range desired | Colonies counted x 100 x (1/ Sample Vol in mL) | Go to tool
6 | pH | Analysis must be done immediately, Grab | pH meter | Calibrate pH meter against at least 2 known buffers that bracket the expected pH value | Meter must be accurate to ± 0.1 units, Sample must fall between buffer values |  | Direct Read
7 | Total Residual Chlorine (TRC), mg/L | Analysis must be done immediately, Grab |  | Spectrophotometer or Colorimeter, TRC reagents | Add reagent to sample, Mix well, Let stand for 3-5 mins, Read results |  | Direct Read
8 | Specific Oxygen Uptake Rate (SOUR), mg/g/hr | Analysis must be done immediately, Grab | Adjust Temp. to ~20°C, Oxygenate sample by vigorous shaking | DO meter/stirrer probe & temp, Stopwatch, BOD bottle | Fill BOD Bottle to overflowing with sample. Insert probe and activate stirrer | After DO stabilizes, read DO level every min. for 15 mins (OR) until DO < 1 mg/L | (DO Uptake Rate/ MLVSS) x 60
9 | Settled Sludge Volume (SSV), mL/L & Sludge Vol Index (SVI) | Analysis must be done immediately, Grab |  | Mallory settleometer or equivalent with stirrer, Thermometer | Mix sample with stirrer, Pull stirrer gently from settleometer, Record settled Sludge Vol every 5 mins | SVI calculated from SSV at 30 mins & MLSS conc. | SSV at 30 mins x 1000 / MLSS

## Design & Operating Parameters
SN | Parameter | Conventional ASP | High Rate ASP | Extended Aeration | Contact Stabilization |  | Step Aeration | Calculation
[5 empty] | Contact | ReAeration
1 | Aeration Detention Time (hrs) | 4 - 8 | 2 - 4 | 18 - 30 | 0.5 - 1.0 | 3 - 6 | 3 - 6 | (Tank Vol, cu. ft) x (7.5 gal/cu. ft) x 24 hrs/day x (1/Flow. MGD)
2 | Aeration Tank Organic Loading (lb BOD/1000 cu. ft) | 25 - 50 | 50 - 100 | 5 - 15 | 30 - 70 | 30 - 70 | 30 - 70 | (Primary Effluent BOD, mg/L) x Flow, MGD x 8.34 x (1/Vol. of Aeration Tank, in 1000s cu. ft)
3 | MLSS (mg/L) | 1500 - 3000 | 1200 - 2500 | 2000 - 6000 | 1000 - 2500 | 4000 - 10000 | 2000 - 3500 | Dry Wt. of Sample (g) x 1000 (mg/g) x 1000 (mL/L) x (1/Sample Size in mL)
4 | F/M Ratio | 0.2 - 0.5 | 0.5 - 1.0 | 0.02 - 0.10 | 0.2 - 0.6 | 0.2 - 0.6 | 0.2 - 0.5 | Primary Effluent BOD, mg/L x Flow, MGD / [(MLVSS x Aeration Tank Vol. in 1000s cu. ft x 8.34 lb/gal)]
5 | Sludge Age (SRT/MCRT), days | 4 - 10 | 2 - 4 | 20 - 40 | 4 - 16 | 4 - 16 | 4 - 10 | MLSS, mg/L x Aeration Tank Vol in 1000s cu ft. x 8.34 x [1/ {(RAS mg/L x WAS, MGD) + Effluent TSS, mg/L x Flow MGD x 8.34})]
6 | Air Requirement (cu ft/ lb BOD removed) | 750 - 1200 | 650 - 850 | 2000 - 3500 | 750 - 1200 | 750 - 1200 | 800 - 850 | Air Applied, cu. ft. / [Primary Effluent BOD x Flow x 8.34]
7 | Oxygen Requirement (lb/lb BOD removed) | 0.8 - 1.1 | 0.7 - 0.9 | 1.4 - 1.6 | 0.8 - 1.2 | 0.8 - 1.2 | 0.6 - 0.8 | Oxygen Applied, lbs / [Primary Effluent BOD x Flow x 8.34]
8 | Respiration Rate - OUR (mg/hr / g MLVSS) | 7 - 15 | 15 - 25 | 3 - 8 | 20 - 30 | 10 - 30 | 8 - 20 | OUR, mg/L/hr x 1000 / MLSS, mg/L
9 | Solids Accumulation Rate (lb/ lb BOD removed) | 0.7 - 0.9 | 0.8 - 1.0 | 0.65 - 0.8 | 0.9 - 1.1 | 0.9 - 1.1 | 0.7 - 0.9 | RAS, mg/L x WAS, MGD x EFF, mg/L x Flow x 8.34 / [(Primary Eff BOD - Secondary Eff BOD, mg/L) x Flow x 8.34]
10 | SVI (mL/g) | 50 - 150 | 50 - 150 | 25 - 110 | 50 - 150 | 50 - 150 | 50 - 150 | SSV (30) x 1000 / MLSS
11 | RAS conc. (mg/L) | 6000 | 6000 | 7500 | 8000 | 8000 | 6000 | Dry Wt. Sample x 1000 mg/g x 1000 mL/L / Sample size, mL
12 | RAS flow (% of influent) | 25 - 75 | 25 - 100 | 50 - 100 | 50 - 125 | 50 - 125 | 25 - 175 | RAS Flow, MGD x 100 / Influent Flow, MGD
13 | Primary Clarifier Overflow Rate (gal/ sq ft/ day) |  |  | 800 - 1200 |  |  |  | Flow / Clarifier Surface Area
14 | Secondary Clarifier Overflow Rate (gal/ sq ft/ day) | 400 - 800 | 400 - 800 | 200 - 400 | 400 - 800 | 400 - 800
15 | Primary Clarifier Detention Time (hrs) |  |  | 1 - 2
16 | Primary Clarifier Depth (ft) |  |  | 10 - 12 |  |  |  | Tank Vol, cu. ft. x 7.5 gal/cu. ft. x 24 / Flow
17 | Secondary Clarifier Depth (ft) |  |  | 1 - 15 |  |  |  | Tank Vol, cu. ft. x 7.5 gal/cu. ft. x 24 / Flow
18 | Clarifier Weir Loading (gal/ft/day) |  |  | 20000 |  |  |  | Flow / Length of Effluent Weir
19 | Solids Loading (lb/day/sq ft) | 20 - 30 | 20 - 30 | 5 - 25 | 20 - 30 | 20 - 30 | 20 - 30 | (Flow + RAS) x MLSS / Clarifier Surface Area

## Calculator
BOD Calc |  |  | TSS Calc |  | Faecal Coliform |  | E coli
INPUT |  |  | INPUT |  | INPUT |  | INPUT
BOD Bottle Volume |  | mL | Sample Volume | mL | Sample Volume | mL | Sample Volume | mL
Sample Volume |  | mL | Weight of Filter+Sample | g | Colonies counted | # | Colonies counted | #
DO initial |  | mg/L | Weight of Filter | g
DO final |  | mg/L
Average daily flow in plant |  | MGD
OUTPUT |  |  | OUTPUT |  | OUTPUT |  | OUTPUT
BOD (in mg/L) |  | mg/L | TSS |  | Faecal Coliform | col / 100 mL | Faecal Coliform | col / 100 mL
BOD (in lbs/day) | 0 | lbs/day