## ConceptFAQs
ABOUT Polymer Dosing
Polymer Dosing is employed for flocculation in order to control Rising or Floating Sludge problems in the Secondary Clarifier, but might result in excess sludge production.

## Calculator
CALCULATION TOOL
INPUT :
Maximum Daily Treated Effluent Flow rate |  | MLD
Maximum Hourly Treated Effluent Flow rate |  | m3/hr
Size of Mixing Tank |  | L
OUTPUT :
For Anionic Polymer, Powder form, 100% strength
Maximum Hourly Treated Effluent Flow rate |  | m3/hr
Maximum Polymer dosage Treatment level | 3 | g/ m3 effluent
Maximum Polymer dosage Treatment level | 0 | g/ hr
Concentration of polymer solution | 1 | g/ m3
Maximum flow rate of feed pump | 0 | L/hr
Diluting water flow rate | 0 | L/hr
Ensure aging time of at least 60 minutes with a max withdrawal rate of 300 L/h
The polymer mixer should have 2 to 3 compartments with a minimum volume of 300 L in the last feed chamber.
SOURCES
https://www.mrwatergeek.com/polymer-dosing/
https://www.fluksaqua.com/en/question/calculating-polymer-concentration/
DILUTION TEST
Stock Solution
Dilution factor table - % solids
JAR Testing
Coagulant - 5,10,15,20,25 ppm
Vol. of sample
GPM... LPM
Speed of Rotor
5 min, 15 min, 60 mins
Prescriptive data
PAANI : Big Data Analysis, Correlation curves