## ConceptFAQs
ABOUT Return Activated Sludfe (RAS)
Return sludge is the liquid pumped from the bottom of the final clarifier back to the aeration tank. If the liquid was not pumped from the bottom of the final clarifier, the
aeration tank. If the liquid was not pumped from the bottom of the final clarifier, the
solids would get deeper and deeper and deeper and soon flow over the effluent weirs.
The return sludge is pumped back to the aeration tank to return the live, hungry bugs on
the bottom of the clarifier back to the aeration tank to continue eating the incoming food.
The objective of return rate control is to optimize the distribution of solids between the
aeration tank and final clarifier and to optimize both functions of the final clarifier:
clarification and thickening.
Clarification is defined as the separation of solid particles and liquid. Thickening is
defined as the increase in solid concentration in which particles move closer to each
other.
Considering the impacts, If the RAS pump was Shut OFF
- The sludge blanket would begin to rise and soon solids would go over the effluent
weirs.
- The aeration basin solids level would decrease and result in an insufficient number of
bugs to eat the incoming BOD.
- The solids in the final clarifier would quickly become anaerobic.
Considering the impacts, If the RAS pump was Fully OPEN
- The sludge on the bottom would be very thin.
- The increased return rate would increase the solids loading and decrease the settling
time in the clarifier.
The optimum rate is somewhere between full open and turned off.
SOURCE : State of Maine Department of Environmental Protection, "Notes on Activated Sludge Process Control"

## Calculator
CALCULATION TOOL
Based on Mass Balance in Secondary Clarifier |  | Based on SSV, SSC, SVI, or SDI |  | Based on Sludge Quality |  | Based on State Point Analysis Method
(Q + Qr) x MLSS = (Qr x RASc) + (Qw x WASc) |  | Qr = (Q + Qr) x SSV / 1000 |  | I. Conduct Sludge settling test using Settleometer
Q x MLSS + Qr x MLSS = Qr x RASc + Qw x WASc |  | Qr x 1000 = Q x SSV + Qr x SSV |  | II. Keep noting the Settled Sludge Volume (SSV, in mL/L) at different times (in mins)
Qr = [ (Qw x WASc) - (Q x MLSS) ] / (MLSS - RASc) |  | Qr = Q x SSV / (1000 - SSV) |  | (NOTE - if it's a 2 L settleometer, divide the observed settled volume by 2)
where, |  | Qr = Q x [ MLSS x 1000 / SSC ] / (1000 - [ MLSS x 1000 / SSC ] ) |  | III. Calculate the Settled Sludge Conc. (SSC, in mg/L) using the following:
Q = Average daily flow to Aeration Tank, MGD |  | Qr = Q x MLSS x 1000 / { (1000 x SSC) - ( MLSS x 1000 ) } |  | SSC = MLSS x 1000 / SSV
Qr = Average daily RAS flow, MGD |  | Qr = Q x SSV / (1000 - SSV) |  | where, MLSS = Avg. Mixed Liquor Suspended Solids in each Aeration Tank, in mg/L
Qw = Average daily WAS flow, MGD |  | Qr = Q x [SVI x MLSS / 1000] / (1000 - [SVI x MLSS / 1000]) |  | IV. Draw a smooth graph of SSC (in 1000 mg/L) vs Time (in mins). It should look like this :
MLSS = Avg Mixed Liquor Suspended Solids in each AT, mg/L |  | Qr = Q x SVI x MLSS / { 10^6 - (SVI x MLSS) }
WASc = WAS concentration, mg/L |  | Qr = Q x [100/SDI] x MLSS / {10e6 - ([100/SDI] x MLSS) }
RASc = RAS concentration, mg/L |  | Qr = Q x 100 x MLSS / { (10^6 x SDI) - (100 x MLSS) }
where,
INPUT : |  | Q = Average daily flow, MGD
Average daily flow to Aeration Tank | MGD | Qr = RAS flow, MGD |  |  |  | SOURCES
Average daily WAS flow | MGD | MLSS = Avg Mixed Liquor Suspended Solids in each AT, mg/L |  |  |  | https://www.maine.gov/dep/water/wwtreatment/state_point_article.pdf
Average MLSS in each Aeration Tank | mg/L | SSV = Settled Sludge Volume in Settleometer, mL/L |  |  |  | State of Maine Department of Environmental Protection, "Notes on Activated Sludge Process Control"
WAS or RAS concentration | mg/L | SSC = Settled Sludge Concentration in Settleometer, mg/L
SVI = Sludge Volume Index, mL/g
OUTPUT : |  | SDI = Sludge Density Index, g/100 mL
Average daily RAS flow | MGD | 1000 is 1000 mL/L
Avg daily RAS flow as % of Avg daily flow to Aeration Tank | % | 1000 is 1000 mg/g
10^6 is 10^6 mLmg/Lg
V. Circle the "Knee Area" and note the associated Time & SSV/SSC. These are optimum values.
|  | INPUT : |  | Optimum time ranges are given below when usually, 70-80% of the sludge has settled.
|  | Average daily flow to Aeration Tank | MGD | Rapid Settling Sludge : 15 - 30 mins
|  | Average MLSS in each Aeration Tank | mg/L | Normal Settling Sludge : 40 - 60 mins
|  | Settled Sludge Volume in Settleometer (SSV), if known | mL/L | Slow Settling Sludge : 100 - 140 mins
|  | Settled Sludge Concentration in Settleometer (SSC), if known | mg/L | VI. The Optimum SSC is the desired RAS/WAS concentration.
|  | Sludge Volume Index (SVI), if known | mL/g | VII. Adjust RAS flow till your current RAS conc. reaches the desired RAS conc. determined above.
|  | Sludge Density Index (SDI), if known | g/100 mL | If your current RAS conc. < Desired RAS conc., Decrease the RAS flow gradually
If your current RAS conc. > Desired RAS conc., Increase the RAS flow gradually
OUTPUT :
|  | Average daily RAS flow, based on SSV | MGD | VIII. OR you could use the tool below to determine the Ideal RAS flow you need to set :
|  | Avg daily RAS flow as % of Avg daily flow to Aeration Tank | % | Qr = Q x MLSS x 1000 / { (1000 x SSC) - ( MLSS x 1000 ) }
where,
|  | Average daily RAS flow, based on SSC | MGD | Q = Average daily flow to Aeration Tank, in MGD
|  | Avg daily RAS flow as % of Avg daily flow to Aeration Tank | % | Qr = Average daily RAS flow, in MGD
MLSS = Avg Mixed Liquor Suspended Solids in each AT, mg/L
|  | Average daily RAS flow, based on SVI | MGD | SSC = Optimum Settled Sludge concentration determined, mg/L
|  | Avg daily RAS flow as % of Avg daily flow to Aeration Tank | %
If you know the ideal WAS flow rate for your system, use the following formula instead
|  | Average daily RAS flow, based on SDI | MGD | Qr = [ (Qw x SSC) - (Q x MLSS) ] / (MLSS - SSC)
|  | Avg daily RAS flow as % of Avg daily flow to Aeration Tank | % | where,
Qw = Average daily WAS flow, in MGD
INPUT :
|  |  |  | Optimum Sludge Settling Time | mins
|  |  |  | Optimum Sludge Settling Concentration | mg/L
|  |  |  | MLSS | mg/L
|  |  |  | Average daily flow to Aeration Tank | MGD
|  |  |  | Average daily WAS flow, if known | MGD
OUTPUT :
|  |  |  | Optimum Average daily RAS flow, if WAS flow not known | MGD
|  |  |  | Avg daily RAS flow as % of Avg daily flow to Aeration Tank | %
|  |  |  | Optimum Average daily RAS flow, if WAS flow known | MGD
|  |  |  | Avg daily RAS flow as % of Avg daily flow to Aeration Tank | %

## Equipment Issues
EQUIPMENT ISSUES
Make sure to carry out the following action items before process control.
At RAS line
1. Inspection in case of breakdown of Pumps or Motors
2. Strainers aren’t plugged
3. Valves aren’t stuck
4. Lines aren’t clogged or choked
5. Lines aren’t leaking

## Process Control
PROCESS CONTROL
Two basic methods for RAS flow control to Aeration Tank : | https://doc-0o-2c-apps-viewer.googleusercontent.com/viewer/secure/pdf/4jv2k70ogsdten3d13o4cv5kbp094e12/kqrlf43r20v4qsioic0rdne7062vh4o4/1612159725000/drive/12829417007850323796/ACFrOgA7M8OmAOuG10lcjs2chrTco8mQclG4Z9xpU9QxjCC0g7BGs0W597ZAFIrI7T7hJx3hA3inRRBEsM6i7bZ_U0C3g-RAY4tTkHdHTpcmIuxOhCNMbIPHYXjHCoJU8mwAcvw1jBI2PrVaR5M0?print=true&nonce=6rn5ti4pl3kki&user=12829417007850323796&hash=cf5afhumnq0rnjilnbporgd6on8l6c1v
- Constant Rate of RAS, independent of Influent Flow rate
- Constant % of varying Influent Flow rate
Techniques to determine the optimum return sludge flow rate :
- Clarifier sludge blanket depth
- Secondary clarifier mass balance
- Aeration tank mass balance
- Settleability
- SVI
- Sludge quality
- State point analysis
1. Basic control strategy:
i) Maintain a optimal distribution of solids between the
aeration tank and the secondary clarifier (solids belong in the aeration tank),
ii) Return the solids to the aeration tank quickly (avoid anaerobic conditions),
iii) Optimize the sludge concentration (thickly).
2. Check your plant’s current return sludge flow rate versus typical rates given for your
mode of operation.
3. Select an appropriate control method (i.e., constant rate or constant percentage),
4. All plants should monitor the sludge blankets,
5. Return rate changes should be made whenever: 1) the average daily flow changes, or
2) the sludge settling characteristics change.
6. In most plants, there is a limit to how low the return sludge flow rate can be reduced
before the return sludge piping plugs up.
7. Return sludge flow rate changes should be limited to +/- 15 to 25 percent per day.
8. System response to RAS flow changes are somewhat rapid. Normally, the system
responds within half the aeration detention time.
SOURCE : State of Maine Department of Environmental Protection, "Notes on Activated Sludge Process Control"