## ConceptFAQs
ABOUT Sludge Volume Index (SVI)
Sludge Volume Index (SVI)
The Sludge Volume Index indicates the relative settleability of the sludge. The SVI is defined as the
Volume, in milliliters, occupied by gram of sludge
The SVI is a relative number, but it is useful as index for a given facility. Many factors affect the
“accuracy” of the SVI test. You should not compare plants with it because a “good” range for one
facility may be very poor for another facility: “Good” SVI readings can be 80 - 300+, depending on
plant (clarifiers).
Diluted Settleability
Diluted settleability can be used to differentiate between filamentous or slime bulking and a “glutted”
(too many solids) condition
The MLSS consideration in the SVI calculation for this, includes 50% Aeration Tank MLSS, 50% Secondary Clarifier effluent
Make a dilution of 50% MLSS, 50% unchlorinated clarifier effluent and fill a 2-liter Settleometer
with some of the diluted sample. Fill another 2-liter Settleometer with 100% mixed liquor.
If the diluted sample settles significantly better than full sample there are too many solids in system.
If the settleability of the diluted sample is about the same as the settleability of the undiluted sample,
filamentous or slime bulking is probably occurring.
SOURCE : State of Maine Department of Environmental Protection, "Notes on Activated Sludge Process Control"

## Lab Procedure
LAB PROCEDURE | TEST DATA
Equipment required | Time (min) | SSV (mL/L) | SSC (mg/L) | Comments / Instructive Guide | Observations
A 2-liter Mallory Settleometer with a wide, plastic stirrer | 0 |  |  |  | (a) During the first 5 – 10 minutes:
A laboratory clock | 5 |  |  |  | (i) How does the floc look?
A pipette with a suction bulb | 10 |  |  | Fill in (a) | ___Granular ___Compact
| 15 |  |  |  | ___Fluffy ___Feathery
Procedure | 20 |  |  |  | (ii) What is the size of the agglomerating
1. Collect the sample near aeration tank effluent weirs. | 25 |  |  |  | floc?
2. Collect a sample from each aeration tank. | 30 |  |  | Fill in (b) | ___ Large ___Small
3. Run settling tests immediately after collecting the sample | 40 |  |  |  | (iii) How are the sludge particles
4. Pour fresh well-mixed sample to the line at the top of the settleometer | 50 |  |  |  | settling?
5. Gently mix with wide paddle and stop current | 60 |  |  |  | ___ As a Blanket
6. Start timer for 5 minutes | 90 |  |  | SSV & SSC reading & calculations for a time duration of 90 mins or more, are only required when the sludge settles slowly. | ___ As individual Particles
Caution | 120 |  |  |  | (iv) How does the supernatant look?
– The first 5 minutes are critical | 150 |  |  |  | ___Clear ___Cloudy
– Observe the floc characteristics, channeling | 180 |  |  |  | (v) Is there straggler floc in the
– Observe the supernatant quality | 240 |  |  |  | supernatant?
– Record your observations in log or settling test bench sheet |  |  |  |  | ___ Yes ___ No
– Continue with readings every 5 minutes for the first 30 minutes, then every 10 minutes until 60. |  |  |  |  | If Yes, how much
• Read again in 2 hours |  |  |  |  | ___ Lots ___ Not much
– further compaction?
– floating sludge? |  |  |  |  | (b) At the end of 30 minutes:
• Leave on bench and check after 4 hours |  |  |  |  | How does the sludge blanket look?
– Do you observe floating sludge? |  |  |  |  | ___Crisp ___Homogenous
– Rise in 0.5-1.0 hour indicates significant nitrification/denitrification |  |  |  |  | ___Fluffy ___Like a sponge
– No rise in four hours means little nitrification/denitrification |  |  |  |  | (c) Rise Time ____Hr ____Min
7. Record results in log or on bench sheet
• Graph readings, settled sludge volume, ssv in ml, versus time, in minutes
• Locate “knee of curve” to determine the theoretical optimum settling time
SOURCE : State of Maine Department of Environmental Protection, "Notes on Activated Sludge Process Control"

## Calculator
FORMULA | CALCULATION TOOL
SSC = MLSS x 1000 / SSV | INPUT :
SVI = SSV x 1000 / MLSS (in mg/L) | Volume of settleometer | L
| Time of settling | mins
SSV : Settled Sludge Volume | Volume of settled sludge | mL
SSC : Settled Sludge Concentration | MLSS conc. | mg/L
MLSS : Mixed Liquor Suspended Solids | Clarifier effluent TSS conc. (for diluted SVI) | mg/L
OUTPUT :
| SSV() | mL/L
| SVI | mL/g
| DIluted SVI | mL/g
| SSC | mg/L
| Diluted SSC | mg/L