## Indicators
INDICATORS
Look for any combination of the following indicators of a Toxicity event currently happening : | The pKa for H2S is 7.0, indicating higher toxicity at a pH of 7 or less when H2S is predominant, and less toxicity as the pH increases above pH 7 and H2S dissociates. One mg/L of H2S reduces the activated sludge OUR by 50% at pH 7, and the H2S dose to give a 50% OUR reduction increases to 100 mg/L at pH values above pH 8. It is advised to add lime or other alkaline agent to the aeration basin to raise the pH to 7.5 or above if sulfide toxicity is occurring.
1. Very low or sharp drop in oxygen uptake rate revealed by SOUR test
2. Microscopic Analysis of Mixed Liquor or recyclate samples showing total absence of Protozoa, Rotifers and Ciliates, and generally dead/inactive microorganisms (images). Abundance of Flagellates ("Flagellate Bloom"), Amoebas instead. (images)
3. High Heavy Metal presence in Aeration Tank influent or recycled flow to Aeration Tank or Primaries
4. High Quaternary Ammonia or Sulfide in Aeration Tank influent, mixed liquor or recyclate
5. Unusual chemical odor, color or foam in Aeration Tank influent, mixed liquor or recyclate
6. Temperature of Aeration Tank influent, mixed liquor or recyclate outside the range of 77-95°F (or 25-35 °C)
6. pH of Aeration Tank influent, mixed liquor or recyclate outside the range of 7.0 - 8.5.
7. High/Low Alkalinity in influent, mixed liquor.or recyclate
8. High Conductivity of Aeration Tank influent, mixed liquor or recyclate
9. Sudden increase in DO or ORP (without significant changes in BOD load, MLSS and Blower Output)
10. Light colored Mixed Liquor or recyclate
11. Flocs breaking up in Aeration Tank
12. Rotten Egg smell or High Organic Acid concentration in Aeration Tank influent, mixed liquor or recyclate
13. High Ammonia and low Nitrate or Nitrite concentrations in Aeration Tank effluent
14. Sharp drop in SVI and poor settleability of Mixed Liquor and/or recyclate sample
15. Cloudy or Turbid Secondary Clarifier effluent
16. High BOD/COD, Ammonia, Phosphorus or TSS levels in Secondary Clarifier effluent
17. High TSS in filtrate from Sludge Dewatering System
18. Very dark brown “dead bug” foam
Look for any combination of the following indicators of your system recovering from a recent Toxicity event :
1. High oxygen uptake rate revealed by SOUR test
2. Microscopic Analysis of Mixed Liquor or recyclate samples showing few life forms except for Amoebas, Flagellates and some Free-swimming Ciliates. Additionally, some Zooglea and/or Fungi may be present. (images)
2. Grey & slimy or White & billowy, sudsy, frothy foam or floating sludge on Aeration Tank surface (resembling images)
3. Poor floc formation and presence of light, fluffy Dispersed cells, Straggler floc or tiny, brown Pin flocs in Aeration Tank, Secondary Clarifier, effluent or recyclate (resembling images)
4. Low DO and ORP in Aeration Tank and Dark color of Mixed liquor
5. Rotten Egg smell or High Organic Acid concentration in Mixed liquor
6. High Ammonia and Low Nitrate/Nitrite presence in Aeration Tank effluent
7. Mixed liquor sample settling slowly in Settleometer, presence of straggler floc in supernatant
8. Clouds of fluffy, homogeneous sludge rising in certain areas in Secondary Clarifier
9. Cloudy or Turbid Secondary Clarifier effluent
10. High BOD/COD, Ammonia, Phosphorus or TSS levels in Secondary Clarifier effluent
11. Excessive sludge production
Influent changes due to an increase in toxic substances such as Heavy Metals, Phenols, Chlorinated hydrocarbons, Halogens, Acids & Bases or other Non-Biodegradable, Inhibitory solids may have caused a toxic upset.
High Salinity or Conductivity due to higher dissolved salts may cause corrosion and scale formation.
Examples of toxicity events or sources :-
1. Washing of cement or lime trucks to a manhole,
2. Dumping of congealed diesel fuel to the sewer system,
3. Overloading of high septage wastes,
4. Recirculation of septic solids from sludge dewatering units,
5. Water softening, Truck washes, Cleaners/disinfectants, Anti-freeze (port-a-potty treatments), Wood-weatherproofing, Paints & solvents, Hide tanning, High chloride food industries, Pharmaceutical industries, Storm water with petroleum, chlorides, etc.,
Try to identify & eliminate the source of the toxic load. Preseve Contact consultant for further investigation.