## ConceptFAQs
ABOUT Waste Activated Sludge (WAS)
Sludge wasting represents the operator’s greatest control adjustment. Sludge wasting
affects the following:
- solids inventory
- F/M and Sludge Age
- the production of biological solids
- oxygen consumption
- mixed liquor settleability
- nutrient quantities needed
- the occurrence of foaming
- the possibility of nitrification
The objective of sludge wasting is to control the wasting rate to maintain steady state. In other words: wasting equals the accumulation of solids (net growth + inert nonbiodegradable). If sufficient sludge is not wasted intentionally, it will waste itself in the final effluent until a process equilibrium is reached.
SOURCE : State of Maine Department of Environmental Protection, "Notes on Activated Sludge Process Control"

## Calculator
CALCULATION TOOL
Based on constant MLSS |  | Based on constant F/M Ratio |  |  | Based on constant SRT |  | Sludge Quality Control Method
WASq x RASc x 8.34 = (MLSSc - MLSSt) x 8.34 x ATv |  | WASq x RASc x 8.34 = [ (BOD/FMc) - (BOD/FMt) ] x (1/R) x 8.34 x ATv |  |  | SRT = Solids in AT / Solids leaving ASP |  | To optimize wasting, satisfy interrelated process requirements
WASq = (MLSSc - MLSSt) x ATv x 8.34 / (RASc x 8.34) |  | WASq = ({BOD/FMc} - {BOD/FMt}) x ATv x 8.34 / (R x RASc x 8.34 x Wt) |  |  | SRT = MLSS x 8.34 x ATv / [(Qw x RASc x 8.34) + (Qe x TSS x 8.34)] |  | - Aeration tank observations
where, |  | where, |  |  | (Qw x RASc x 8.34) + (Qe x TSSe x 8.34) = MLSS x 8.34 x ATv / SRT |  | - Secondary clarifier observations
WASq = Average Qty. of solids to be wasted, in gallons |  | WASq = Average Qty. of solids to be wasted, in gallons |  |  | Qw = {1/ (RASc x 8.34) } x { (MLSS x 8.34 x ATv / SRT) - (Qe x TSSe x 8.34) } |  | - Microscopic examination of the MLSS
MLSSc = Current avg MLSS in each Aeration Tank, in mg/L |  | BOD = Current influent BOD to Aeration Tank, in lbs/day |  |  | where, |  | - Mixed liquor settling characteristics
MLSSt = Target avg MLSS in each Aeration Tank, in mg/L |  | FMc = Current F/M Ratio, in lbs/day / lbs |  |  | Qw = Average WAS flow rate, in gal/day |  | - Depth of the sludge blanket
ATv = Avg filled Volume of each Aeration Tank, in gallons |  | FMt = Target F/M Ratio, in lbs/day / lbs |  |  | RASc = RAS/WAS conc., in mg/L |  | - MLSS respiration rates
RASc = RAS/WAS concentration, in mg/L |  | ATv = Avg filled Volume of each Aeration Tank, in gallons |  |  | MLSS = Average MLSS in each Aeration Tank, in mg/L
Wt = Time duration of wasting, in hours |  | R = Ratio of MLVSS to MLSS |  |  | ATv = Avg filled Volume of each Aeration Tank, in gallons
8.34, is 8.34 lbs/gal for every 1 mg/L |  | RASc = RAS/WAS concentration, in mg/L |  |  | Qe = Average Secondary Clarifier Effluent flow rate, in gal/day
|  | Wt = Time duration of wasting, in hours |  |  | TSSe = TSS conc. in Secondary Clarifier Effluent, in mg/L
INPUT : |  | 8.34, is 8.34 lbs/gal for every 1 mg/L |  |  | 8.34, is 8.34 lbs/gal for every 1 mg/L
Current Average MLSS in each Aeration Tank | mg/L
Target Average MLSS in each Aeration Tank | mg/L | INPUT : |  |  | INPUT :
Avg filled Vol. of each Aeration Tank | gal | Influent BOD to Aeration Tank, if known |  | lbs/day | Average MLSS in each Aeration Tank | mg/L
Average RAS/WAS concentration | mg/L | Influent COD to Aeration Tank |  | lbs/day | Avg filled Vol. of each Aeration Tank | gal
Time duration of wasting | hrs | BOD to COD ratio for your facility, if known |  |  | Sludge Retention Time (SRT) | days
|  | Suggested BOD to COD ratio |  |  | Average daily Effluent Flow rate from Secondary Clarifier | gal/day
OUTPUT : |  | Derived Influent BOD to Aeration Tank |  | lbs/day | Average TSS concentration in Secondary Clarifier effluent | mg/L
Average Qty. of solids to be wasted, in gallons | gal | Current F/M Ratio |  |  | Average RAS/WAS concentration | mg/L
Average WAS flow rate, in gal/hr | gal/hr | Target F/M Ratio |  |  | Time duration of wasting per day | hrs
MLVSS to MLSS Ratio for your facility, if known
|  | Suggested MLVSS to MLSS Ratio | 0.8 |  | OUTPUT :
|  | Avg filled Vol. of each Aeration Tank |  | gal | Average WAS flow rate, in gal/day | gal/day
|  | Average RAS/WAS concentration |  | mg/L | Average WAS flow rate, in gal/hr | gal/hr
|  | Time duration of wasting |  | hrs
Based on constant MCRT
|  | OUTPUT : |  |  | MCRT = Solids in AT+SC / Solids leaving ASP
|  | Average Qty. of solids to be wasted, in gallons |  | gal | MCRT = MLSS x 8.34 x (ATv + SCv) / [(Qw x RASc x 8.34) + (Qe x TSS x 8.34)]
|  | Average WAS flow rate, in gal/hr |  | gal/hr | (Qw x RASc x 8.34) + (Qe x TSSe x 8.34) = MLSS x 8.34 x (ATv + SCv) / SRT
Qw = {1/ (RASc x 8.34) } x { (MLSS x 8.34 x (ATv + SCv) / SRT) - (Qe x TSSe x 8.34) }
where,
Qw = Average WAS flow rate, in gal/day
RASc = RAS/WAS conc., in mg/L
MLSS = Average MLSS in each Aeration Tank, in mg/L
ATv = Avg filled Volume of each Aeration Tank, in gallons
SCv = Avg filled Volume of each Secondary Clarifier, in gallons
Qe = Average Secondary Clarifier Effluent flow rate, in gal/day
TSSe = TSS conc. in Secondary Clarifier Effluent, in mg/L
8.34, is 8.34 lbs/gal for every 1 mg/L
INPUT :
[5 empty] | Average MLSS in each Aeration Tank | mg/L
[5 empty] | Avg filled Vol. of each Aeration Tank | gal
[5 empty] | Avg filled Vol. of each Secondary Clarifier | gal
[5 empty] | Mean Cell Residence Time (MCRT) | days
[5 empty] | Average daily Effluent Flow rate from Secondary Clarifier | gal/day
[5 empty] | Average TSS concentration in Secondary Clarifier effluent | mg/L
[5 empty] | Average RAS/WAS concentration | mg/L
[5 empty] | Time duration of wasting per day | hrs
OUTPUT :
[5 empty] | Average WAS flow rate, in gal/day | gal/day
[5 empty] | Average WAS flow rate, in gal/hr | gal/hr

## Equipment Issues
EQUIPMENT ISSUES
Make sure to carry out the following action items before process control.
At WAS line
1. Inspection in case of breakdown of Pumps or Motors
2. Strainers aren’t plugged
3. Valves aren’t stuck
4. Lines aren’t clogged or choked
5. Lines aren’t leaking

## Process Control
PROCESS CONTROL
System response to waste activated sludge rate changes are normally slow. usually from about 1 to 2 SRTs.
Waste sludge changes should be limited to +/- 15 percent per day.