Read Me for key understanding (Concept, Action steps for O&M)

Dissolve Oxygen (DO) Supplementation

This page tells you all you need to know about supplementing DO within your facility.

- How do you monitor for Dissolved Oxygen (DO)?

- Constantly monitor the supplied air flow rates and DO levels (every few hours, until a pattern is established). Check to see the DO concentrations are the same, increasing or decreasing as you adjust air flow rates accordingly. A good sign of a problem is when these are out of sync and control becomes difficult.

- Consider changes in aeration mode for your type of loading and capacity. Plug flow, Step-aeration, Tapered aeration usually work for high organic loads or higher F/M requirements, while Continuous mix, Contact Stabilization work for lower F/M requirements and greater resilience against toxic upsets due to slug loads.

- A higher F/M ratio requires greater DO and air supply, due to the faster oxygen consumption. Try to reduce or account for increased influent loading by enforcing sewer use ordinances, pre-treatment program, increasing the number of blowers or aerators, motors, equalizations basins and/or aeration basins on-line. This may be required during winters when microbial activity slows down. Reduce or take off-line accordingly for reduced loading.

- Check for signs of poor mixing which can include:

- Still or stagnant zones, which can appear more dark

- Low DO

- Biomass or solids in layers

- Solids accumulation on the basin floor

- What are ways to augment Dissolved Oxygen (DO)?

- Once you have checked all the above and are unable to increase DO any further, you can augment your oxygen supplied by using dosing chemicals like Hydrogen Peroxide (H2O2), Potassium Permanganate (KMnO4) or Chlorine, which act as strong oxidants.

- The next page features a DO Supplementation calculator that computes how much H2O2 or KMnO4 you’ll need to dose based on your target air supply and deficit.

- How do you ensure effective operation & maintenance of your chemical dosing system for DO supplementation?

- Ensure your flowmeters are cleaned and calibrated from time to time

- Ensure hand valves manually adjusted to regulate flow are not stuck. For automated flow adjustments by the VFD (Variable Frequency Drive) on your pump-motors, regularly check the settings on your HMI in the control panel. Perform manual checks using flow meters from time to time to ensure the instrumentation works accurately.

- Ensure your standby devices, pumps, etc. are in good operating condition, ready to go in case of breakdowns. Have them installed in parallel.

- Regularly clean your lines to prevent them from plugging or choking.