## Calculator
Calculation Tool : Bioaugmentation
Bioaugmentation is a way to supplement your liquor with more bugs, if the organic loading is too much or there's a process upset. This improves settleability and treatment efficiency. There are two ways to compute the bioaugmentation requirement that are specified below. For more urgent needs, the dosage recommended is in the range of 1-10 mg/L. If an introductory dose is used, the dosage is usually ≥ 2 ppm up to 4 ppm or more and may be applied for 2-4 days before reducing the dosage rate. If your treatment goal is less urgent, and just to improve the health and viability of your bugs, use a dosage of 1-2 ppm. Note : You might also have to increase sludge wasting as you supply more bugs to the liquor.
INPUTS
Influent Flow to Aeration Basin (MGD) | 0.5 | MGD
Volume of Aeration Basin (gallons) | 400000 | gallons
MLVSS concentration (mg/L or ppm) | 2400 | mg/L or ppm
Bioaugmentation dosage rate (mg/L or ppm) Recommended introductory dose : 4 mg/L | 4 | mg/L or ppm
Duration of bioaugmentation program (days) Recommended: 12 days | 12 | days
METHODS
Method 1: Based on influent flow | This method works if you need to meet discharge permit requirements urgently.
Method 2: Based on Bioreactor volume | This method is the more cost-effective.
OUTPUTS
Method 1
Amount of solids (lbs/day) for the first 2-4 days | 16.68 | lbs/day
Amount of solids (lbs/day) for the next 2-4 days | 8.34 | lbs/day
Amount of solids (lbs/day) for the remaining days of the bioaugmentation program | 4.17 | lbs/day
Method 2
Amount of solids (lbs/day) for all days of the bioaugmentation program | 13.344 | lbs/day