## Summary
Sludge Return Flow based on Mass Balance Principle : Solids entering Aeration Basin = Solids leaving Aeration Basin
where,
Target F(RAS) = Target RAS Flow (MGD or million gal/day)
F(AB) = Total Flow entering Aeration Basins (MGD or million gal/day). This will be computed from the inputs below.
SSV = Settled Sludge Volume (mL or milliliters) - This is the sludge volume measured after sufficient or ideal settling time in the settleometer
V(settleometer) = Volume of Settleometer (L or liters)
Guide to selecting the right settling time (for the right RAS concentration)
The standard settling time applied is 30 mins
Guideline values for different sludges :
Rapid Settling Sludge : 15-30 mins
Normal Settling Sludge : 40-60 mins
Slow Settling Sludge : 100-140 mins
For more accurate results, you need to develop Setttled Sludge Concentration Curves.
Click here for detailed analysis.
INPUTS - Enter values for the following where missing :
Flows:
Total Flow entering Aeration Basins including RAS (MGD or million gal/day) | 0.52 | MGD or million gal/day
Current RAS Flow (MGD or million gal/day) | 0.2 | MGD or million gal/day
Other:
Ideal settling time considered (minutes) | 30 | minutes
Settled Sludge Volume (SSV) after ideal settling time (mL) | 300 | mL
Volume of Settleometer (L) | 2 | L
Minutes of operation of Secondary WAS pump per hour, on average | 20 | minutes
OUTPUTS | MGD (million gallons per day) | Gallons per day (GPD) | GPM (gallons per minute)
Your Target RAS Flow : | 0.078 | 78000 | 54.1667
Your Current RAS Flow : | 0.2 | 200000 | 138.8889
Required change in RAS Flow : | -0.122 | -122000 | -84.7222
Changes in RAS Flow should be no more than 10-15% per day. Modify RAS flow rate as per the schedule below : | Required change in MGD (million gallons per day) | Required change in GPD (gallons per day) | Required change in GPM (gallons per minute)
Day 1 | -0.025 | -25000 | -17.3611
Day 2 | -0.021875 | -21875 | -15.191
Day 3 | -0.019141 | -19140.625 | -13.2921
Day 4 | -0.016748 | -16748.0469 | -11.6306
Day 5 | -0.014655 | -14654.541 | -10.1768
Day 6 | -0.012823 | -12822.7234 | -8.9047
Day 7 | -0.01122 | -11219.883 | -7.7916
Day 8 | -0.00053918 | -539.1808 | -0.37443
Day 9
Day 10

## Extra 1
Sludge Return Flow based on Mass Balance Principle : Settled Sludge Concentration Curves
Graph of Settled Sludge Conc. (mg/L) vs Time (mins) This is what your graph would look like, depending on how fast your sludge settles.
where,
SSC = Settled Sludge Concentration (mg/L)
MLSS = Mixed Liquor Suspended Solids (mg/L)
Vol(s) = Volume of Settleometer (L)
SSV = Settled Sludge Volume (mL) - This is the sludge volume measured after sufficient settling time in the settleometer
INPUTS - Enter values for the following where missing :
Total Flow entering Aeration Basins (MGD or million gal/day) | 0.5 | MGD or million gal/day
Mixed Liquor Suspended Solids (MLSS) | 2500 | mg/L or ppm
Volume of Settleometer (Vol(s)) | 2 | L (Liters)
Now, only enter the SSV values in the table below after each of the settling time durations. The SSC values will be computed automatically. |  |  |  | Your Settled Sludge Concentration Curve below:
Settling Time Duration (mins) | SSV (mL) | SSC (mg/L) | Comments
0 | 2000 | 2500
5 | 1500 | 3333
10 | 1200 | 4167
15 | 1000 | 5000
20 | 850 | 5882
25 | 700 | 7143
30 | 600 | 8333
40 | 580 | 8621
50 | 570 | 8772
60 | 565 | 8850
90
120
150
180
240
OUTPUTS | MGD (million gallons per day) | Gallons per day (GPD) | GPM (gallons per minute) | INPUTS (Contd.)
Your Ideal Return Sludge Flow Rate (RAS) : | 0.10606 | 106058.035 | 73.6514 | Locate the "Knee of the Curve" on your graph. Record the corresponding time (x-axis) for this Knee or Bend. Record the corresponding SSC (y-axis) for this Knee or Bend.
Your Current Return Sludge Flow Rate (RAS) : | 0.085 | 85000 | 59.0278 | Ideal Sludge Settling Time | 30 | mins
Required change in RAS Flow Rate : | 0.021058 | 21058.035 | 14.6236 | Ideal Settled Sludge Conc. (SSC) | 14286 | mg/L
The SSC recorded here will be your ideal RAS concentration, and the target RAS flow is computed from the formula below:
Changes in RAS Flow should be no more than 10-15% per day. Modify RAS flow rate as per the schedule below : | Required change in MGD (million gallons per day) | Required change in GPD (gallons per day) | Required change in GPM (gallons per minute)
Day 1 | 0.010625 | 10625 | 7.3785 | where,
Day 2 | 0.010433 | 10433.035 | 7.2452 | Qr = Return Flow rate (MGD or million gallons per day)
Day 3 |  |  |  | Qi = Influent Flow to AB (MGD) = Primary Effluent Flow - Diverted Flow
Day 4 |  |  |  | Ideal SSC = Settled Sludge conc. after ideal settling time (mg/L or ppm)
Day 5 |  |  |  | MLSS = Mixed Liquor Suspended Solids (mg/L or ppm)
Day 6
Day 7
Day 8
Day 9
Day 10

## O&M
Action Items for O&M
Ensure the following :
Inspection in case of breakdown of Pumps or Motors
Strainers aren’t plugged
Valves aren’t stuck
Lines aren’t clogged or choked
Lines aren’t leaking