Read Me for key understanding (Concept, Action steps for O&M)

O&M - General

This page provides a brief checklist of general O&M action items to keep your treatment units running effectively.

- Ensure your flowmeters are cleaned and calibrated from time to time

- Ensure hand valves manually adjusted to regulate flow are not stuck. For automated flow adjustments by the VFD (Variable Frequency Drive) on your pump-motors, regularly check the settings on your HMI in the control panel. Perform manual checks using flow meters from time to time to ensure the instrumentation works accurately.

- Ensure your standby devices, pumps, etc. are in good operating condition, ready to go in case of breakdowns. Have them installed in parallel.

- Regularly clean your lines to prevent them from plugging or choking. Solids deposition can cause problems downstreams with reduced flows, surface seeding of filaments, septicity, etc. Influent septicity can also corrode parts of the pipe. All of this necessitates regular inspection.

- Check your lines for wear & tear, and leaks and get sections repaired or replaced accordingly.

- Constantly monitor the supplied air flow rates and DO levels (every few hours, until a pattern is established). Check to see the DO concentrations are the same, increasing or decreasing as you adjust air flow rates accordingly. A good sign of a problem is when these are out of sync and control becomes difficult.

- Ensure accurate DO measurements by regularly checking calibration of your DO meters or probes, and cleaning the probes and monitoring equipment.

- Check if the surface aeration pattern is uniform in your Aerators. Check for surging of the water surface or turbulence.

- Clean and remove any scum, fibers, debris, dust, solids deposited on the diffuser ports. These can cause premature wear & tear and failure.

- Clean, repair, replace air filters to keep head losses to a minimum.

- Document all maintenance and repairs thoroughly.

- Add more clarifiers on-line or in parallel to handle varying flow volumes and adjust hydraulic retention times. Adding more clarifiers in series or parallel will increase the overall retention time, and vice versa.

- Ensure RAS mechanism is working optimally: Hydraulic suction, Tow-Brow. Brush or push solids into RAS hoppers on a regular basis.

- Inspect RAS (Return Activated Sludge) suction tubes, ensure there's no plugging or clogging in the RAS line.

- Ensure the Clarifier Center-well is aligned correctly.

- Ensure the Clarifier overflow weirs are level and aligned correctly. Raise weirs during high flow events.

- Ensure the Scraper or rake arm is moving at regular speed (1-2 rotations per hour, typically) as per design, without any jerking in rotation.

- Perform regular scheduled preventive maintenance.

- Sludge Removal (every 1-2 years) – Digester system must be cleaned. Remove any excess sludge, either manually or automatically.

- Pump Clearing (every 3-6 months) – When pumping high solids content waste, ensure that pumps are cleared of debris regularly, which can clog pumps hindering operation of the digester.

- Check the hydraulic station every time before starting the filter press to check if the hydraulic oil is sufficient and in normal state, especially in winters, when the oil can freeze.

- Regularly inspect the filter press control box for any damage, since the working environment of the filter press is generally harsh, often in contact with humid air. During winters, place some dry substances in the control box for suction air moisture.