## Cover
Waste Activated Sludge (WAS)
The ideal WAS flow rate can be determined in five different ways depending on your priority design number. Click on the computation method you prefer.
Your Priority Design Number : | Constant MCRT (includes solids in clarifier)
WAS computation based on constant MCRT | Click here for calculator
WAS computation based on constant SRT | Click here for calculator
WAS computation based on constant MLSS | Click here for calculator
WAS computation based on constant F/M Ratio | Click here for calculator
WAS computation based on constant Yield | Click here for calculator

## WAS_MCRT
Sludge Wasted based on Constant MCRT
where,
Target F(WASs) = Target Secondary WAS Flow (GPM or gallons per minute)
C(RAS) = Avg RAS concentration (mg/L or ppm)
Solids inventory AB, SC = Solids inventory in Aeration Basin and Secondary Clarifier (lbs per day). This will be computed from the inputs below.
MCRT = Mean Cell Residence Time, ie, The avg. time a bug stays in the secondary treatment stage - Aeration Basins and Secondary Clarifiers (days)
F(SCw) = Effluent Flow Rate at Secondary Clarifier Weirs (MGD)
C(DL) = Weekly TSS Discharge Limit (mg/L or ppm)
T(WASs) = Minutes of operation of Secondary WAS pump per hour, on average
INPUTS - Enter values for the following where missing :
Design:
Design or Target MCRT (days) | 3 | days
Weekly TSS Discharge Limit (mg/L or ppm) | 30 | mg/L or ppm
Capacities:
Total Volume of Aeration Basins (million gal) | 0.5 | million gal
Total Volume of Secondary Clarifiers (million gal) | 0.35 | million gal
Avg Sidewater Depth of Secondary Clarifiers (feet) | 14 | feet
Flows:
Total Flow leaving Secondary Clarifiers (MGD or million gal/day) | 1 | MGD or million gal/day
Current Secondary WAS Flow (GPM or gal/minute) | 95 | GPM (gal/minute)
Concentrations:
Avg. MLSS concentration (mg/L or ppm) | 3200 | mg/L or ppm
Avg. RAS concentration (mg/L or ppm) | 9000 | mg/L or ppm
Other:
Avg. Sludge Blanket Depth (feet) | 11 | feet
Minutes of operation of Secondary WAS pump per hour, on average | 20 | minutes
OUTPUTS
Solids Inventory in Aeration Basins | 13344 | lbs/day
Solids Inventory in Secondary Clarifiers | 3815.55 | lbs/day
| MGD (million gallons per day) | GPD (gallons per day) | GPM (gallons per minute)
Your Target Secondary WAS Flow : | 0.07287 | 72870.3704 | 151.8133
Your Current Secondary WAS Flow : | 0.0456 | 45600 | 95
Required change in Secondary WAS Flow : | 0.02727 | 27270.3704 | 56.8133
Changes in WAS Flow should be no more than 10-15% per day. Modify WAS flow rate as per the schedule below : | Required change in MGD (million gallons per day) | Required change in GPD (gallons per day) | Required change in GPM (gallons per minute)
Day 1 | 0.0057 | 5700 | 11.875
Day 2 | 0.0064125 | 6412.5 | 13.3594
Day 3 | 0.0072141 | 7214.0625 | 15.0293
Day 4 | 0.0079438 | 7943.8079 | 16.5496
Day 5
Day 6
Day 7
Day 8
Day 9
Day 10

## WAS_SRT
Sludge Wasted based on Constant SRT
where,
Target F(WASs) = Target Secondary WAS Flow (GPM or gallons per minute)
C(RAS) = Avg RAS concentration (mg/L or ppm)
Solids inventory AB = Solids inventory in Aeration Basins (lbs/day). This will be computed from the inputs below.
SRT = Solids Retention Residence Time, ie, The avg. time a bug stays in the secondary treatment stage - Aeration Basins only (days)
F(SCw) = Effluent Flow Rate at Secondary Clarifier Weirs (MGD)
C(DL) = Weekly TSS Discharge Limit (mg/L or ppm)
T(WASs) = Minutes of operation of Secondary WAS pump per hour, on average
INPUTS - Enter values for the following where missing :
Design:
Design or Target SRT (days) | 3 | days
Weekly TSS Discharge Limit (mg/L or ppm) | 30 | mg/L or ppm
Capacities:
Total Volume of Aeration Basins (million gal) | 0.5 | million gal
Total Volume of Secondary Clarifiers (million gal) | 0.35 | million gal
Avg Sidewater Depth of Secondary Clarifiers (feet) | 14 | feet
Flows:
Total Flow leaving Secondary Clarifiers (MGD or million gal/day) | 1 | MGD or million gal/day
Current Secondary WAS Flow (GPM or gal/minute) | 95 | GPM or gal/minute
Concentrations:
Avg. MLSS concentration (mg/L or ppm) | 3200 | mg/L or ppm
Avg. RAS concentration (mg/L or ppm) | 9000 | mg/L or ppm
Other:
Avg. Sludge Blanket Depth (feet) | 11 | feet
Minutes of operation of Secondary WAS pump per hour, on average | 20 | minutes
OUTPUTS
Solids Inventory in Aeration Basins | 13344 | lbs/day
| MGD (million gallons per day) | GPD (gallons per day) | GPM (gallons per minute)
Your Target Secondary WAS Flow : | 0.055926 | 55925.9259 | 116.5123
Your Current Secondary WAS Flow : | 0.0456 | 45600 | 95
Required change in Secondary WAS Flow : | 0.010326 | 10325.9259 | 21.5123
Changes in WAS Flow should be no more than 10-15% per day. Modify WAS flow rate as per the schedule below : | Required change in MGD (million gallons per day) | Required change in GPD (gallons per day) | Required change in GPM (gallons per minute)
Day 1 | 0.0057 | 5700 | 11.875
Day 2 | 0.0046259 | 4625.9259 | 9.6373
Day 3
Day 4
Day 5
Day 6
Day 7
Day 8
Day 9
Day 10

## WAS_MLSS
Sludge Wasted based on Constant MLSS
where,
Target F(WASs) = Target Secondary WAS Flow (GPM or gallons per minute)
Current F(WASs) = Current Secondary WAS Flow (GPM or gallons per minute)
C(RAS) = Avg RAS concentration (mg/L or ppm)
Actual Solids AB,SC = Current solids inventory in your Aeration Basins and Secondary Clarifiers. This will be computed from the inputs below.
Target Solids AB,SC = Target solids inventory in your Aeration Basin and Secondary Clarifiers, combined, based on Target or Design MLSS. This will be computed from the inputs below.
T(WASs) = Minutes of operation of Secondary WAS pump per hour, on average
INPUTS - Enter values for the following where missing :
Design:
Design or Target MLSS concentration (mg/L or ppm) | 2400 | mg/L or ppm
Capacities:
Total Volume of Aeration Basins (million gal) | 0.5 | million gal
Total Volume of Secondary Clarifiers (million gal) | 0.35 | million gal
Avg Side-Water Depth of Secondary Clarifiers (feet) | 14 | feet
Flows:
Current Secondary WAS Flow (GPM or gal/minute) | 95 | GPM or gal/minute
Concentrations:
Avg. MLSS concentration (mg/L or ppm) | 2000 | mg/L or ppm
Avg. RAS concentration (mg/L or ppm) | 9000 | mg/L or ppm
Other:
Avg. Sludge Blanket Depth (feet) | 11 | feet
Minutes of operation of Secondary WAS pump per hour, on average | 40 | minutes
OUTPUTS | Aeration Basin (lbs) | Secondary Clarifiers (lbs) | Combined (lbs)
Actual solids inventory | 8340 | 3440.25 | 11780.25
Target solids inventory | 10008 | 3565.35 | 13573.35
Total Solids to be wasted (Actual - Target) | -1668 | -125.1 | -1793.1
| MGD (million gallons per day) | GPD (gallons per day) | GPM (gallons per minute)
Your Target Secondary WAS Flow : | 0.067311 | 67311.1111 | 70.1157
Your Current Secondary WAS Flow : | 0.0912 | 91200 | 95
Required change in Secondary WAS Flow : | -0.023889 | -23888.8889 | -24.8843
Changes in WAS Flow should be no more than 10-15% per day. Modify WAS flow rate as per the schedule below : | Required change in MGD (million gallons per day) | Required change in GPD (gallons per day) | Required change in GPM (gallons per minute)
Day 1 | -0.0114 | -11400 | -11.875
Day 2 | -0.009975 | -9975 | -10.3906
Day 3 | -0.0025139 | -2513.8889 | -2.6186
Day 4
Day 5
Day 6
Day 7
Day 8
Day 9
Day 10

## WAS_FM
Sludge Wasted based on Constant F/M Ratio
where,
Target F(WASs) = Target Secondary WAS Flow (GPM or gallons per minute)
Current F(WASs) = Current Secondary WAS Flow (GPM or gallons per minute)
F(AB) = Total Flow entering Aeration Basins (MGD or million gallons per day)
C(BODi) = BOD concentration in Aeration Basin Influent (mg/L or ppm)
Actual FM = Actual F/M Ratio, based on influent BOD and existing solids inventory in Aeration Basin. This will be computed from the inputs below.
Target FM = Target F/M Ratio, based on influent BOD and target solids inventory in Aeration Basin
C(RAS) = Avg RAS concentration (mg/L or ppm)
T(WASs) = Minutes of operation of Secondary WAS pump per hour, on average
INPUTS - Enter values for the following where missing :
Design:
Design or Target F/M Ratio | 0.4
Capacities:
Total Volume of Aeration Basins (million gal) | 0.5 | million gal
Flows:
Total Flow entering Aeration Basins including RAS (MGD or million gal/day) | 1 | MGD or million gal/day
Current Secondary WAS Flow (GPM or gal/minute) | 95 | GPM or gal/minute
Concentrations:
Avg. BOD concentration in Aeration Basin Influent (mg/L or ppm) | 250 | mg/L or ppm
Avg. MLVSS concentration (mg/L or ppm) | 2400 | mg/L or ppm
Avg. RAS concentration (mg/L or ppm) | 9000 | mg/L or ppm
Other:
Minutes of operation of Secondary WAS pump per hour, on average | 40 | minutes
OUTPUTS
Actual F/M Ratio | 0.20833
Design or Target F/M Ratio | 0.4
| MGD (million gallons per day) | GPD (gallons per day) | GPM (gallons per minute)
Your Target Secondary WAS Flow : | 0.15509 | 155088.8889 | 161.5509
Your Current Secondary WAS Flow : | 0.0912 | 91200 | 95
Required change in Secondary WAS Flow : | 0.063889 | 63888.8889 | 66.5509
Changes in WAS Flow should be no more than 10-15% per day. Modify WAS flow rate as per the schedule below : | Required change in MGD (million gallons per day) | Required change in GPD (gallons per day) | Required change in GPM (gallons per minute)
Day 1 | 0.0114 | 11400 | 11.875
Day 2 | 0.012825 | 12825 | 13.3594
Day 3 | 0.014428 | 14428.125 | 15.0293
Day 4 | 0.016232 | 16231.6406 | 16.908
Day 5 | 0.0090041 | 9004.1233 | 9.3793
Day 6
Day 7
Day 8
Day 9
Day 10

## WAS_Yield
Sludge Wasted based on Yield : Sludge wasted = Amount of solids produced
where,
Target F(WASs) = Target Secondary WAS Flow (GPM or gallons per minute)
F(AB) = Total Flow entering Aeration Basins (MGD)
F(SCw) = Total Flow leaving Secondary Clarifier Weirs (MGD)
C(BODi) = Avg. BOD concentration in Aeration Basin Influent (mg/L or ppm)
C(BODw) = Avg. BOD concentration at Weirs of Secondary Clarifiers (mg/L or ppm)
C(DL) = Weekly TSS Discharge Limit (mg/L or ppm)
C(RAS) = Avg. RAS concentration (mg/L or ppm)
Y = Yield coefficient (Amount of solids removed for every lb of BOD removed)
T(WASs) = Minutes of operation of Secondary WAS pump per hour, on average
INPUTS - Enter values for the following where missing :
Design:
Design or Target Yield Coefficient (Y) if known (typically, 0.7) | 0.7
Weekly TSS Discharge Limit (mg/L or ppm) | 30 | mg/L or ppm
Flows:
Total Flow entering Aeration Basins including RAS (MGD or million gal/day) | 1 | MGD or million gal/day
Total Flow leaving Secondary Clarifier Weirs (MGD or million gal/day) | 0.97 | MGD or million gal/day
Current Secondary WAS Flow | 30 | GPM or gal/minute
Concentrations:
Avg. BOD concentration in Aeration Basin Influent (mg/L or ppm) | 250 | mg/L or ppm
Avg. BOD concentration at Weirs of Secondary Clarifiers (mg/L or ppm) | 25 | mg/L or ppm
Avg. RAS concentration (mg/L or ppm) | 8000 | mg/L or ppm
Other:
Minutes of operation of Secondary WAS pump per hour, on average | 20 | minutes
OUTPUTS | MGD (million gallons per day) | GPD (gallons per day) | GPM (gallons per minute)
Your Target Secondary WAS Flow : | 0.016116 | 16115.625 | 33.5742
Your Current Secondary WAS Flow : | 0.0144 | 14400 | 30
Required change in Secondary WAS Flow : | 0.0017156 | 1715.625 | 3.5742
Changes in WAS Flow should be no more than 10-15% per day. Modify WAS flow rate as per the schedule below : | Required change in MGD (million gallons per day) | Required change in GPD (gallons per day) | Required change in GPM (gallons per minute)
Day 1 | 0.0017156 | 1715.625 | 3.5742
Day 2
Day 3
Day 4
Day 5
Day 6
Day 7
Day 8
Day 9
Day 10

## O&M
Action Items for O&M
Ensure the following :
Inspection in case of breakdown of Pumps or Motors
Strainers aren’t plugged
Valves aren’t stuck
Lines aren’t clogged or choked
Lines aren’t leaking