## Summary
Aeration Requirements for Process Control
INPUTS :
A. Flow and Polluting Parameters
Design
1 | Are you mandated to Nitrify, Denitrify? Select accordingly. | Yes - Nitrification & Denitrification
2 | Weekly BOD Discharge Limit (mg/L or ppm) | 10 | mg/L or ppm
3 | Weekly TSS Discharge Limit (mg/L or ppm) | 30 | mg/L or ppm
4 | Weekly Total Nitrogen (TN) Discharge Limit (mg/L or ppm) | 4 | mg/L or ppm
Capacities
5 | Total Volume of Aeration Basins (million gal) | 0.4 | million gal
Flows
6 | Total Flow entering Aeration Basins including RAS (MGD or million gal/day) | 0.5 | MGD or million gal/day
7 | RAS Flow (MGD or million gal/day) | 0.1 | MGD or million gal/day
8 | Primary WAS Flow (GPM or gal/minute) | 25 | GPM or gal/minute
9 | Avg. BOD concentration in combined Aeration Basin Influent (mg/L or ppm) | 15 | GPM or gal/minute
10 | Filtrate from Sludge thickening, dewatering (GPD or gal/day) | 25000 | GPD or gal/day
Concentrations
11 |  | 250 | mg/L or ppm
12 | Avg. Total Nitrogen (TN) concentration in combined Aeration Basin Influent (mg/L or ppm) | 35 | mg/L or ppm
13 | Avg. MLVSS concentration (mg/L or ppm) | 1800 | mg/L or ppm
14 | Avg. TSS concentration in RAS (mg/L or ppm) | 7000 | mg/L or ppm
15 | Avg. TSS concentration in Primary WAS (mg/L or ppm) | 12000 | mg/L or ppm
16 | Avg. TSS concentration in Filtrate from Sludge thickening, dewatering (mg/L or ppm) | 1600 | mg/L or ppm
Other
17 | Minutes of operation of Primary WAS pump per hour, on average | 20 | minutes
18 | Minutes of operation of Secondary WAS pump per hour, on average | 15 | minutes
B. Environmental Data
1 | Altitude (Elevation) at job site (feet) (h) | 1000 | feet
2 | T = Temperature at job site (°C) | 30 | °C
3 | Tw = Process temperature of wastewater (°C) | 27 | °C
4 | Select measurement parameter of wastewater salt concentration | Salinity
5 | Salt concentration of wastewater (ppt or parts per trillion) | 5 | ppt
C. Aeration & DO
1 | Select the type of Aeration System you use | Fine Bubble Diffusers (1-3 mm bubbles)
2 | Select your specific aeration equipment | Diffused Aeration - Coarse Bubble
3 | Depth of diffuser submergence, in feet (if you use a diffuser system) (d) | 5 | feet
4 | Enter the desired DO to be maintained in the mixed liquor (typically, 2 mg/L and a minimum of 1 mg/L) | 2 | mg/L or ppm
5 | The existing DO in your mixed liquor (mg/L or ppm) | 1.5 | mg/L or ppm
6 | Your current total air flow rate - for diffuser system (cfm) and/or | 6000 | cfm
7 | Your current total power input (hp) | 200 | hp
PROCEDURE :
To determine the total air needed for your bugs, the following computations are made :
# | Computation | Purpose | Link
1 | AOR (Actual Oxygen Requirement) | Total Oxygen required for design organic loading | Click here to know how it's done.
2 | SOR (Standrad Oxygen Requirement) | Total Oxygen required for design organic loading, for the aeration equipment used and the site conditions. | Click here to know how it's done.
3 | Design Air Flow, Pressure, Power, Efficiency, Turndown | Total Air Flow, Power required under field conditions | Click here to know how it's done.
OUTPUT :
1 | Maximum total Air flow requirement, in cfm | 7464.6012 | cfm
2 | Minimum Total Air flow requirement for mixing, process requirements, in cfm | 802.0911 | cfm
3 | Your current total air flow - for diffuser system (cfm) | 6000 | cfm
4 | Maximum total Power requirement (hp) | 545.5131 | hp
5 | Minimum Power requirement (hp) | 58.6168 | hp
6 | Your current total power input (hp) | 200 | hp
7 | Design Discharge Pressure | 4.915 | psi
8 | Avg Blower Efficiency or Efficiency of overall system | 29.37%
9 | Avg Blower Turndown | 1:10 or 89%

## 1. AOR
I. Estimating AOR (Actual Oxygen Requirement)
To determine how much air your equipment needs to supply, you need to start with determining how much oxygen your bugs need for digesting organic matter (substrate metabolism), decomposition (endogenous respiration) and/or nitrification-denitrifiction.
where,
Ltotal = Total oxygen required per day (lbs/day)
LBOD = Oxygen required per day for BOD removal (lbs/day)
LN = Oxygen required per day for Nitrification (lbs/day)
LDN = Oxygen recovered per day through Denitrification (lbs/day)
Oxygen required for BOD removal (LBOD) accounts for both substrate digestion and endogenous respiration. The proportions vary depending on the F/M Ratio illustrated below.
F/M Ratio (lbs BOD per day/ lb VSS) | Oxygen consumed for BOD removal (lbs O2/lb BOD removed)
0.05 | 1.3
0.1 | 1.2
0.2 | 1.1
0.5 | 1
1 | 0.9
5 | 0.7
Nitrification-Denitrification Processes | Proportion of Oxygen (lbs O2/lbs N) | Consumed / Recovered | Notes
Nitrification | 4.6 | Consumed | Oxidizes N in Ammonia -> NO3
Dentrification | 2.86 | Recovered | Reduces NO3 -> N2
Sludge production |  |  | 8% of solids is Nitrogen by weight, leaving 92% that gets oxidized and reduced
OUTPUTS
Daily Oxygen Requirement
Operating F/M Ratio | 0.17361
Oxygen consumed for 1 lb BOD removed (from graph) | 1.1299 | lbs O2/lb BOD
Biological sludge produced | 1182.612 | lbs SS/day
LBOD = Total O2 consumed for BOD removal | 1177.8904 | lbs O2/day
LN = Total O2 consumed for Nitrification | 236.1688 | lbs O2/day
LDN = Total O2 recovered from Denitrification | 109.1867 | lbs O2/day
Ltotal = Total O2 consumed per day (AOR) | 1304.8725 | lbs O2/day
1. The computed oxygen demand is not evenly distributed through the day. Oxygen requirements for endogenous respirtation are uniform over 24 hours. For substrate digestion, nitrification and denitrification, the oxygen requirements vary depending on the influent flow, so a Peaking Factor (PF) is applied depending on the Population Equivalent (PE) - ie, the total number of people contributing to the organic load. 2. The Oxygen requirements for BOD removal (LBOD) involves both Substrate Digestion, Endogenous respiration. The breakup depends on the F/M ratio in the table below:
F/M Ratio | Oxygen for Substrate Digestion | Oxygen for Endogenous Respiration
<= 0.2 | 40% | 60%
> 0.2 | 60% | 40%
Target Organic Load Removal | 1009.5904 | lbs BOD/day
Population Equivalent (PE) for your total organic load, at minimum of 80 g or 0.17 lbs/person/day | 5938.7668 | PE
Peaking Factor (PF) | = 4.7.(PE^ -0.11), where PE = Population Equivalent
Peaking Factor (PF) for your facility | 1.8071
Avg Hourly Flow to Aeration Basin | 20833.3333 | gallons per hour
Peak Hourly Flow = Avg Hourly Flow x PF | 37648.704 | gallons per hour
Hourly Oxygen Requirement | Peak requirement (lbs O2/hr)
LBOD(sub) = Total Oxygen consumed for Substrate Digestion | 35.4768
LBOD(er) = Total Oxygen consumed for Endogenous Respiration | 29.4473
LN = Total O2 consumed for Nitrification | 17.7829
LDN = Total O2 recovered from Denitrification | 8.2215
Ltotal = Total O2 consumed per day (AOR) | 74.4855
Your aeration system must be able to transfer 74 lbs of Oxygen per hour to the mixed liquor, to meet permit requirements.

## 2. SOR
II. Estimating SOR (Standard Oxygen Requirement)
1. You have determined the actual oxygen requirement (AOR) under field conditions. 2. However, the capacity of aeration systems are given by the manufacturer under standard conditions: a DO concentration of 0 mg/L, pure (tap) water at 20°C (68°F), 29.92 inches barometric pressure (atmospheric pressure), 0% relative humidity. This is called the standard oxygen requirment (SOR). 3. In the Aeration Basin, the oxygenating capacity of the equipment is reduced by anywhere between 25-75% due to the effect of salts, surfactants, residual DO > 0 mg/L, temperature, pressure, etc. This would require correction factors to be applied to the AOR to determine the SOR. Ballpark figs. can be used in the absence of specific data on the environmental conditions and aeration equipment used.
Ballpark Figures:
Aeration System | AOR / SOR (typical figs.)
Fine bubble diffusers | 0.33
Medium bubble diffusers | 0.4
Coarse bubble diffusers | 0.5
Mechanical surface aerator | 0.72
Detailed Calculation:
Click here to know more.
OUTPUTS : Correction factors & Final result
α = Wastewater Correction Factor for Oxygen Transfer | 0.65 | TABLE 1
F = Fouling factor | 0.7 | TABLE 1
β = Wastewater Correction Factor for Oxygen Solubility | 0.95 | TABLE 1
c = Depth correction factor for a diffuser system (if you use one) | 0.33 | TABLE 1
Pstd = Barometric pressure at Mean Sea Level (in of mercury) | 28.87 | in Hg (TABLE 3)
Pamb = Barometric pressure at the job site (in of mercury) | 27.8953 | inches of Hg (FORMULA)
Pvap = Vapor pressure, caused due to evaporation at temperature T | 0.42958 | meters of H2O (FORMULA)
Ω = Pressure Correction Factor for Oxygen Saturation | 0.96624 | FORMULA
CsT = DO saturation value at water temp, (mg/L or ppm), zero salt conc | 7.58 | mg/L or ppm (TABLE 4, user input Tw)
Cs20 = DO saturation value of water at std 20°C, (mg/L) zero salt conc | 9.09 | mg/L or ppm (CONSTANT)
τ = Temperature Correction Factor for Oxygen Saturation | 0.83388 | FORMULA
θ = Temperature Correction Factor for Oxygen Transfer | 1.028 | TABLE 2
M = Molar mass of air | 0.02896 | kg/mol CONSTANT
g = Gravitational constant | 9.807 | m/s^2 CONSTANT
R = Molar gas constant | 8.3143 | N.m/(mol.K) CONSTANT
Csc = Depth corrected standard DO saturation value | 9.1366 | mg/L or ppm FORMULA
AOR = Actual Oxygen Requirement (lbs oxygen per day) | 74.4855 | lbs O2/hr
AOR/SOR ratio (computed or referenced) | 0.30171 | lbs O2/hr
SOR = Standard Oxygen Requirement (lbs oxygen per day) | 246.879 | lbs O2/hr
Accounting for the conditions on site, your aeration system must be able to transfer 247 lbs of Oxygen per hour to the mixed liquor, to meet permit requirements.

## 3. Performance
III. Estimating Aearator Performance Parameters
1. For mechanical surface aeration, the power required can be determined based on typical standard aeration efficiencies (SAE) and AOR/SOR ratio. 2. For diffuser systems, the air flow (cfm) and pressure (psi) requirements will be computed from the SOR, AOR and typical standard oxygen transfer efficiencies (SOTE). Discharge pressure required will be determined from depth of submergence, and head losses. 3. Blower horsepower will be determined based on typical standard aeration efficiencies (SAE) and AOR/SOR ratio. Turndown range will be determined from maximum and minimum air requirements.
where,
Air Flow (cfm) : Required air flow in cubic feet per minute (cfm)
d : Depth of submergence (feet)
% O2 : Percentage of oxygen in dry air, by weight (23.2%)
ρ(air) : Density of dry air in standard conditions (0.075 lbs/cubic feet)
SOR : Standard Oxygen Requirement in standard conditions (lbs O2/hr)
AOR : Actual Oxygen Requirement in field conditions (lbs O2/hr)
AOTE : Actual Oxygen Transfer Efficiency in field conditions (for diffused aeration) in %
SOTE : Standard Oxygen Transfer Efficiency in standard conditions (for diffused aeration) in %
SOTE(unit) : Standard Oxygen Transfer Efficiency in standard conditions (for diffused aeration) per foot of submergence, in %
SAE : Standard Aeration Efficiency in standard conditions (lbs O2/hp.hr)
FAE : Field Aeration Efficiency in field conditions (lbs O2/hp.hr)
Pressure (psi) : Discharge pressure required (in pounds per square inch or psi)
Pd : Pressure resulting from the depth of submergence in water (psi)
Ploss : Pressure resulting from head losses over fan, impeller, suction, piping system (length, velocity, valves), fouling, etc. Assumed to be 2.75 psi
Power (hp) : Total Power required of Diffuser or Mechanical Surface Aeration system (hp)
Blower efficiency : Average operating efficiency of blowers (%)
Blower turndown : Operating range or capability of individual blower or entire blower system (as ratio, or %)
Qmax : Maximum Design Air Flow for process requirements (cfm)
Qmin : Minimum Design Air Flow for process requirements (mixing, oxidation, etc.), (cfm)
Click here to know more about Oxygen transfer rates, Aeration efficiencies and Minimum air flow requirements for different aeration equipment.
OUTPUTS
for Blowers or Diffused Aeration :
Design Process Volume in Aeration Basin (million gal) | 0.4 | million gal USER INPUT
d = Depth of diffuser submergence (feet) | 5 | feet USER INPUT
AOR/SOR ratio | 0.30171 | BASED ON SOR Sheet
SOR = Standard Oxygen Requirement (lbs oxygen per day) | 246.879 | lbs O2/hr BASED ON SOR Sheet
SOTE(unit) = Standard Oxygen Transfer Efficiency (%/ft submergence) | 2.1% | % per ft of submergence TABLE 5
SOTE = Standard Oxygen Transfer Efficiency (%) | 10.5% | FORMULA
AOTE : Actual Oxygen Transfer Efficiency (%) | 3.168% | FORMULA
% O2 : Percentage of oxygen in dry air, by weight | 23.2% | CONSTANT
ρ(air) : Density of dry air in standard conditions (lbs/cubic feet) | 0.075 | lbs/ft3 CONSTANT
SAE : Standard Aeration Efficiency in standard conditions (lbs O2/hp.hr) | 1.5 | lbs O2/hp.hr TABLE 6
FAE : Field Aeration Efficiency in field conditions (lbs O2/hp.hr) | 0.45256 | lbs O2/hp.hr FORMULA
Maximum Total Air flow Requirement, in cfm (Qmax) | 7464.6012 | cfm FORMULA
Minimum Total Air flow Requirement for mixing, process requirements, in cfm (Qmin) | 802.0911 | cfm (TABLE 7)
Design Discharge Pressure (Pressure) | 4.915 | psi FORMULA
Maximum Total Power required (hp) (Power_max) | 545.5131 | hp FORMULA
Minimum Total Power required (hp) (Power_min) | 58.6168 | hp FORMULA in Word Doc
Avg Blower Efficiency or Efficiency of overall system | 29.37% | FORMULA
Avg Blower Turndown | 1:10 or 89% | FORMULA
for Mechanical Surface Aeration :
Design Process Volume in Aeration Basin (million gal) | 0.4 | million gal
AOR/SOR ratio | 0.30171
SOR = Standard Oxygen Requirement (lbs oxygen per day) | 246.879 | lbs O2/hr
SAE : Standard Aeration Efficiency in standard conditions (lbs O2/hp.hr) | N/A | lbs O2/hp.hr
FAE : Field Aeration Efficiency in field conditions (lbs O2/hp.hr) | N/A | lbs O2/hp.hr
Maximum Total Power required (hp) | N/A | hp
Minimum Total Power required (hp) for mixing, process requirements | N/A | hp (TABLE 7)

## Tables
SOR (Standard Oxygen Requirement) calculation from AOR (Actual Oxygen Requirement)
where,
AOR = actual oxygen requirement (lbs/day)
SOR = standard oxygen requirement (lbs/day)
α = Wastewater Correction Factor for Oxygen Transfer Oxygen transfer depends on the quantity and type of suspended solids in the water, as these change the viscosity and density of the liquid and the mixing capacity of the device. The α-factor express the ratio between the oxygen mass transfer coefficients for wastewater compared to that for the same device in clean water (KLa wastewater / KLa tap water). The value depends on aeration system and design configuration.
F = Fouling factor, accounts for the loss of oxygen transfer efficiency due to the buildup or scaling of biological and/or chemical film or deposits on the surface of aeration equipment.
β = Wastewater Correction Factor for Oxygen Solubility, used to correct for the dissolved solids in wastewater. The solubility of oxygen in wastewater is 95 to 99 percent of that of pure water.
Ω = Pressure Correction Factor for Oxygen Saturation, accounts for variations in oxygen transfer efficiency due to changes in DO due to pressure changes.
τ = Temperature Correction Factor for Oxygen Saturation
Csc = Depth corrected standard DO saturation value, mg/L
Cs20 = DO saturation value of water at standard temperature of 20°C, zero salt concentration, (mg/L)
CsT = DO saturation value of water at process temperature, zero salt concentration, mg/L
CL = Desired DO concentration of the wastewater, (mg/L)
θ = Temperature Correction Factor for Oxygen Transfer
Tw = Process temperature of wastewater (°C)
c = Depth correction factor for the diffuser system
d = Depth of diffuser, in feet
Pamb = Barometric pressure at the job site (inches of mercury, or PSI)
Pstd = Barometric pressure at Mean Sea Level (29.92 in or 14.7 PSIA)
Pvap = Vapor pressure, caused due to evaporation at temperature T (in meters of water column)
M = Molar mass of air, 0.02896 kg/mol
g = Gravitational constant, 9.807 m/s^2
h = Elevation at job site, in meters
R = Molar gas constant, 8.3143 N.m/(mol.K)
T = Temperature at job site (°C)
REFERENCE TABLES, GRAPHS
Table 1: α, β, F, c correction factors based on Aeration system
Aeration System | α Range | Typical α Value | β Range | Typical β Value | F Range | Typical F Value | Typical c Value
Fine bubble diffusers (no N-DN) | 0.40 to 0.45 | 0.425 | 0.95 to 0.99 | 0.95 | 0.50 to 1.00 | 0.7 | 0.33
Fine bubble diffusers (N only) | 0.55 to 0.65 | 0.55 | 0.95 to 0.99 | 0.95 | 0.50 to 1.00 | 0.7 | 0.33
Fine bubble diffusers (N-DN) | 0.65 to 0.75 | 0.65 | 0.95 to 0.99 | 0.95 | 0.50 to 1.00 | 0.7 | 0.33
Medium bubble diffusers | 0.50 to 0.70 | 0.6 | 0.95 to 0.99 | 0.95 | 0.8 | 0.8 | 0.29
Coarse bubble diffusers | 0.70 to 0.80 | 0.75 | 0.95 to 0.99 | 0.95 | 1 | 1 | 0.25
Mechanical surface aerator | 0.95 to 1.00 | 0.95 | 0.95 to 0.99 | 0.95 | 1 | 1
Table 2: θ variation with Temperature
Temperature Range (T) | θ Value
5°C to < 20°C | 1.024
20°C to < 35°C | 1.028
35°C to 45°C | 1.031
Table 3: Atm. Pressure vs Altitude (for Pstd)
Altitude (feet) | P(std) (inches)
-1000 | 31
-500 | 30.5
0 | 29.92
500 | 29.39
1000 | 28.87
1500 | 28.33
2000 | 27.82
3000 | 26.81
4000 | 25.85
5000 | 24.9
6000 | 23.98
7000 | 23.1
8000 | 22.22
9000 | 21.39
10000 | 20.58
Table 4: Surface oxygen solubility for different temp. (Tw), salt conc. (Chlorinity or Salinity in ppt (parts per trillion))
Chlorinity (ppt) ➡ | 0 | 5 | 10 | 15 | 20 | 25
Salinity (ppt) ➡ | 0 | 9.0328 | 18.0655 | 27.0983 | 36.131 | 45.1638
Temp (°C) ⬇ | DO (mg/L) ⬇ | DO (mg/L) ⬇ | DO (mg/L) ⬇ | DO (mg/L) ⬇ | DO (mg/L) ⬇ | DO (mg/L) ⬇
0 | 14.62 | 13.73 | 12.89 | 12.1 | 11.36 | 10.66
1 | 14.22 | 13.36 | 12.55 | 11.78 | 11.07 | 10.39
2 | 13.83 | 13 | 12.22 | 11.48 | 10.79 | 10.14
3 | 13.46 | 12.66 | 11.91 | 11.2 | 10.53 | 9.9
4 | 13.11 | 12.45 | 11.61 | 10.92 | 10.27 | 9.66
5 | 12.77 | 12.02 | 11.32 | 10.66 | 10.03 | 9.44
6 | 12.45 | 11.73 | 11.05 | 10.4 | 9.8 | 9.23
7 | 12.14 | 11.44 | 10.78 | 10.16 | 9.58 | 9.02
8 | 11.84 | 11.17 | 10.53 | 9.93 | 9.36 | 8.83
9 | 11.56 | 10.91 | 10.29 | 9.71 | 9.16 | 8.64
10 | 11.29 | 10.66 | 10.06 | 9.49 | 8.96 | 8.45
11 | 11.03 | 10.41 | 9.84 | 9.29 | 8.77 | 8.28
12 | 10.78 | 10.18 | 9.62 | 9.09 | 8.59 | 8.11
13 | 10.54 | 9.96 | 9.42 | 8.9 | 8.41 | 7.95
14 | 10.31 | 9.75 | 9.22 | 8.72 | 8.24 | 7.79
15 | 10.08 | 9.54 | 9.03 | 8.54 | 8.08 | 7.64
16 | 9.87 | 9.34 | 8.84 | 8.37 | 7.92 | 7.5
17 | 9.67 | 9.15 | 8.67 | 8.21 | 7.77 | 7.36
18 | 9.47 | 8.97 | 8.5 | 8.05 | 7.62 | 7.22
19 | 9.28 | 8.79 | 8.33 | 7.9 | 7.48 | 7.09
20 | 9.09 | 8.62 | 8.17 | 7.75 | 7.35 | 6.96
21 | 8.92 | 8.46 | 8.02 | 7.61 | 7.21 | 6.84
22 | 8.74 | 8.3 | 7.87 | 7.47 | 7.09 | 6.72
23 | 8.58 | 8.14 | 7.73 | 7.34 | 6.96 | 6.61
24 | 8.42 | 7.99 | 7.59 | 7.21 | 6.84 | 6.5
25 | 8.26 | 7.85 | 7.46 | 7.08 | 6.72 | 6.39
26 | 8.11 | 7.71 | 7.33 | 6.96 | 6.62 | 6.28
27 | 7.97 | 7.58 | 7.2 | 6.85 | 6.51 | 6.18
28 | 7.83 | 7.44 | 7.08 | 6.73 | 6.4 | 6.09
29 | 7.69 | 7.32 | 6.96 | 6.62 | 6.3 | 5.99
30 | 7.56 | 7.19 | 6.85 | 6.51 | 6.2 | 5.9
31 | 7.43 | 7.07 | 6.73 | 6.41 | 6.1 | 5.81
32 | 7.31 | 6.96 | 6.62 | 6.31 | 6.01 | 5.72
33 | 7.18 | 6.84 | 6.52 | 6.21 | 5.91 | 5.63
34 | 7.07 | 6.73 | 6.42 | 6.11 | 5.28 | 5.55
35 | 6.95 | 6.62 | 6.31 | 6.02 | 5.73 | 5.46
36 | 6.84 | 3.52 | 6.22 | 5.93 | 5.65 | 5.38
37 | 6.73 | 6.42 | 6.12 | 5.84 | 5.56 | 5.31
38 | 6.62 | 6.32 | 6.03 | 5.75 | 5.48 | 5.23
39 | 6.52 | 6.22 | 5.98 | 5.66 | 5.4 | 5.15
40 | 6.41 | 6.12 | 5.84 | 5.58 | 5.32 | 5.08
41 | 6.31 | 6.03 | 5.75 | 5.49 | 5.24 | 5.01
42 | 6.21 | 5.93 | 5.67 | 5.41 | 5.17 | 4.93
43 | 6.12 | 5.84 | 5.58 | 5.33 | 5.09 | 4.86
44 | 6.02 | 5.75 | 5.5 | 5.25 | 5.02 | 4.79
45 | 5.93 | 5.67 | 5.41 | 5.17 | 4.94 | 4.72
Table 5: Standard Oxygen Transfer Efficiencies (SOTE unit) per ft submerged
Diffuser System | SOTE (%/ft)
Fine bubble diffusers | 2.1%
Medium bubble diffusers | 1.4%
Coarse bubble diffusers | 0.9%
Table 6: Standard Aeration Efficiencies (SAE)
Equipment | SAE Range (lbs O2/hp.hr) | Typical SAE (lbs O2/hp.hr)
Mechanical Surface Aeration - Surface low-speed | 2.5 to 3.5 | 3
Mechanical Surface Aeration - Surface low-speed with draft tube | 2.0 to 4.6 | 3.3
Mechanical Surface Aeration - Surface high-speed | 1.8 to 2.3 | 2.05
Mechanical Surface Aeration - Submerged turbine with draft tube | 2.0 to 3.3 | 2.65
Mechanical Surface Aeration - Submerged turbine | 1.8 to 3.5 | 2.65
Mechanical Surface Aeration - Submerged turbine with sparger | 2.0 to 3.3 | 2.65
Mechanical Surface Aeration - Horizontal rotor | 1.5 to 3.6 | 2.55
Mechanical Surface Aeration - Other |  | 2.6929
Diffused Aeration - Fine Bubble | 2.0 to 3.3 | 2.65
Diffused Aeration - Medium Bubble | 1.6 to 2.6 | 2.1
Diffused Aeration - Coarse Bubble | 1.0 to 2.0 | 1.5
Diffused Aeration - Tubular System or Static Tube | 2.0 to 2.6 | 2.3
Diffused Aeration - Jet | 2.0 to 4.0 | 3
Diffused Aeration - Aspirator Jet | 2.5 to 4.0 | 3.25
Diffused Aeration - U-Tube | 2.1 to 4.0 | 3.05
Diffused Aeration - Other |  | 2.55
Table 7: Minimum Aeration Requirements
Diffused Aeration | Qmin,unit (m3 / 1000 m3.min) | Qmin,unit (cfm / million gal)
Fine bubble diffused aeration | 15 | 2005.2277
Medium bubble diffusers | 20 | 2673.6369
Coarse bubble diffusers | 20 | 2673.6369
Mechanical surface aeration | Pmin,unit (kW / 1000 m3) | Pmin,unit (hp/gal)
Mechanical surface aerator | 15 | 76.1436