## Calculator
CALCULATION TOOL
Total Flow entering Aeration Basins including RAS (MGD or million gal/day) | 2 | MGD or million gal/day
Avg. BOD concentration in Aeration Basin Influent (mg/L or ppm) | 300 | mg/L or ppm
Avg. Total Inorganic Nitrogen (TIN) concentration in Aeration Basin Influent (mg/L or ppm) | 25 | mg/L or ppm
Avg. Ortho-Phosphate concentration in Aeration Basin Influent (mg/L or ppm) | 1 | mg/L or ppm
Avg. Iron concentration in Aeration Basin Influent (mg/L or ppm) | 0.5 | mg/L or ppm
Minutes of operation of Nutrient dosing pump, per hour on average | 10 | minutes
OUTPUTS :
Suggested BOD : N : P : Iron Ratio | 100 : 5 : 1 : 0.5
| INFLUENT | RESIDUAL | TOTAL
Total Nitrogen requirement (mg/L or ppm) | 15 | 1 | 16
Total Phosphorus requirement (mg/L or ppm) | 3 | 0.5 | 3.5
Total Iron requirement (mg/L or ppm) | 1.5 | 0.1 | 1.6
Nitrogen is sufficient. No dosing required.
More Phosphorus required. Refer below for dosing amounts.
More Iron required. Refer below for dosing amounts.
Recommended Nutrient Dosing Chemicals | % Purity | Molecular Weight Ratio | Density (lbs/gal)
Anhydrous Ammonia, (for N) | 80 | 1.2143 | 6.34
Trisodium phosphate, (for P) | 75 | 5.2903 | 18
Ferric chloride, (for Fe) | 39 | 2.9018 | 11.93
Recommended Nutrient Dosing Rates | GPD (gal/d) | GPM (gal/min) | mL/min
Anhydrous Ammonia, commercial grade 80% conc. | 0 | 0 | 0
Triosodium phosphate, commercial grade 75% conc. | 16.3412 | 0.068088 | 257.7426
Ferric chloride, commercial grade 39% conc. | 11.4432 | 0.04768 | 180.489