Read Me for key understanding (Concept, Action steps for O&M)

Nutrient availability

This page tells you all you need to know about maintaining enough nutrients in your wastewater and its importance.

- What are the key nutrients that your bugs require?

- Nitrogen (N)

- Phosphorus (P)

- Iron (Fe)

- How does nutrient deficiency or excess affect your facility’s performance?

Nutrient deficiency

- Like humans, your bugs need critical nutrients to perform functions like digestion, reproduction, etc. In the absence of enough nutrients, their metabolism slows down and the BOD goes untreated.

- In case of a nutrient deficiency, a slime tends to form around the floc which interferes with the settling and causes foaming problems when aerated.

- Among higher life-forms, flagellates especially are susceptible to deficiency in nitrogen. A large number of flagellates in an advanced stage of the activated sludge process indicates the presence of a large amount of soluble organic nutrients.

Nutrient excess

- However, you can’t overcompensate by having too much nutrient concentration. The BOD and nutrients need to be maintained at low levels just enough to promote stationary growth or starvation, because this leads to floc-formation. Flocs bunch up together when food is low, enabling the sludge solids to settle down and separate from water.

- Batch addition of excess nutrients, for example of nitrogen, can create denitrification problems or lead to excess TSS or nutrient levels in your effluent, causing permit violations.

- How do you measure nutrient concentrations?

Test kits and strips are commercially available for measuring :

- Forms of Nitrogen (N) as Ammonia, Nitrate, Nitrite,

- Phosphorus (P) as Orthophosphate

- Iron

Ensure your test kits are cleaned and calibrated from time to time, per the product manual. Lab methods for testing each of these nutrients are explained in brief below.

- Test for TIN or Total Inorganic Nitrogen = 
Ammonia-N (NH3-N) + Nitrate-N (NO4-N) + Nitrite-N (NO3-N)

- Test for Ammonia-N (NH3-N): EPA Method 350.1

A brief summary is given below (Source: EPA). For details, refer to EPA Method 350.1 : Determination of Ammonia-Nitrogen by Semi-Automated Colorimetry.

- Reagents required: 
Ammonia-free water, Permanent ammonia standards, Standard ammonium chloride, Nessler reagent, Sodium hydroxide (12 N), Copper sulfate solution (10%)

- Procedure:

  - Place 100 mL of the sample in a Nessler tube and add 1 mL of Copper sulfate solution

  - Mix by stirring and rotating. Add 1 mL of Sodium hydroxide.

  - Mix again and allow to settle.

  - Pipette a measured portion of the clear supernatant liquor (ideally 25 mL) depending on the ammonia content into a second Nessler tube and dilute to 100 mL with ammonia-free water

  - If permanent ammonia standards are available, go to the next step. Otherwise, prepare temporary standards by adding 0.2, 0.4, 0.6, 0.8, 1.0, 1.4, 1.7, 2.0, 2.5, 3.0 mL of Standard ammonium chloride to Nessler tubes and dilute to 100 mL with ammonia-free water.

  - Add 2 mL of Nessler reagent to the sample, and to each temporary standard (if used)

  - After 10 minutes, compare the colors and record the standard having color nearest to that of the sample.

- Calculations:

  - For permanent standards:
Ammonia-N (mg/L) =

Amount of Ammonia-NItrogen (NH3-N) in permanent standard (mg) x 1000 / Volume of supernatant used in step iv (mL)

  - For temporary standards:
Ammonia-N (mg/L) =

Volume of Standard ammonium chloride (NH4Cl) in temporary standard (mL) x 10 / Volume of supernatant used in step iv (mL)

- Test for Nitrite-N (NO2-N): EPA Method 353.2, 353.3, 1686

A brief summary is given below (Source: EPA). For details, refer to EPA Method 353.2 : Determination of Nitrite/Nitrate-Nitrogen by Automated Colorimetry, or 353.3 : Nitrogen, Nitrate-Nitrite (Spectrophotometric Cadmium Reduction) or Method 1686.

- Reagents required: 
Nitrite-free water, Aluminum hydroxide, Standard sodium nitrite, Sulfanilic acid, A-naphthylamine

- Procedure:

  - If the sample is colored or turbid, clarify 150 mL by adding 2 mL of aluminum hydroxide.

  - Place a measured portion of the filtrate (10-50) mL, depending on the nitrite content, into a 100 mL Nessler tube and make up to the mark with distilled water.

  - If permanent standards are available, go to the next step. Otherwise, prepare temporary standards by adding 0.2, 0.4, 0.6, 0.8, 1.0, 1.4, 1.7, 2.0, 2.5, 3.0 mL of Standard sodium nitrite to Nessler tubes and dilute to 100 mL with nitrite-free water.

  - Add 2 mL of Sulfanilic acid and 2 mL of A-naphthylamine to the sample and to each temporary standard if used.

  - Mix and allow to stand for 10 minutes. Compare the colors and record the standard having color nearest to that of the sample.

- Calculations:

  - For permanent standards:
Nitrite-N (mg/L) =

Amount of Nitrite-NItrogen (NO2-N) in permanent standard (mg) x 1000 / Volume of filtrate used in step ii (mL)

  - For temporary standards:
Nitrite-N (mg/L) =

Volume of Standard sodium nitrite (NaNO2) in temporary standard (mL) x 0.5 / Volume of sample used (mL)

- Test for Nitrate-N (NO3-N): EPA Method 353.2, 353.3, 1686

A brief summary is given below (Source: EPA). For details, refer to EPA Method 353.2 : Determination of Nitrite/Nitrate-Nitrogen by Automated Colorimetry, or 353.3 : Nitrogen, Nitrate-Nitrite (Spectrophotometric Cadmium Reduction) or Method 1686.

You will first need to determine the CHLORIDE concentration of your sample.

- Reagents required: 
Standard Silver nitrate solution (1 mL equivalent of 0.5 mg chloride ion), Potassium chromate indicator (5%), Chloride-free sodium bicarbonate

- Procedure:

    - Pipette 50 or 100 mL of the sample into an Erlenmeyer flask or porcelain casserole depending on the chloride content

    - Add 1 mL Potassium chromate indicator

    - Titrate first to permanent red color with Standard Silver nitrate. If more than 7 or 8 mL of Silver nitrate is required, repeat the procedure using a smaller sample diluted to 50 mL with Chloride-free distilled water

- Calculations:

  - Chloride (mg/L) =

(Volume of Silver nitrate (mL) - Blank) x 500 / 
Volume of sample used (mL)

Now you will need to REMOVE CHLORIDE per the procedure below.

- Reagents required: 
Standard Silver nitrate solution (Prepare this by dissolving 4.40 grams of Silver sulfate, free from nitrate, in distilled water and dilute to 1 L)

- Procedure:

    - Treat 100 mL of the sample with Standard Silver sulfate solution; 1 mL of Standard Silver sulfate solution should be added for each mg of chloride determined previously.

    - Remove the precipitated chloride by either filtration or by centrifugation. Formation of the precipitate may be aided by heating the solution.

Now you may test for NITRATE-N per the procedure below.

- Reagents required: 
Phenoldisulfonic acid, Sodium hydroxide (12 N), Standard nitrate solution

- Procedure:

    - Filter 30 to 35 mL of the sample through filter paper.

    - Evaporate 25 mL of the filtrate to dryness on a water bath (use a smaller amount if the nitrate content is high)

    - Moisten the residue with 1 mL of Phenoldisulfonic acid.

    - Dilute to about 20 mL with distilled water.

    - Add 12 N Sodium hydroxide until the maximum yellow color is developed (not more than 5 to 6 mL of Sodium hydroxide will be required)

    - Filter into a 100 mL Nessler tube and rinse the dish and paper with distilled water. Add the filtered rinsings to the filtrate and make up to the mark with distilled water.

    - If permanent standards are available, proceed to the next step. Otherwise, make up temporary standards by placing 0.2, 0.4, 0.6, 0.8, 1.0, 2.0, 3.0, 4.0 and 5.0 mL of Standard Sodium nitrate solution in 100 mL Nessler tubes and adding 2 mL of 50% Sodium hydroxide.

    - Dilute to the mark with distilled water.

    - Compare the color and record the standard having color nearest to that of the sample.

- Calculations:

  - For permanent standards:
Nitrate-N (mg/L) =

Amount of Nitrate-NItrogen (NO3-N) in permanent standard (mg) x 1000 / Volume of sample used (mL)

  - For temporary standards:
Nitrate-N (mg/L) =

Volume of Standard sodium nitrate (NaNO3) in temporary standard (mL) x 10 / Volume of sample used (mL)

Now combine the three to determine the Total Inorganic Nitrogen (TIN)

Total Inorganic Nitrogen (TIN) = 
Ammonia-N (NH3-N) + Nitrate-N (NO4-N) + Nitrite-N (NO3-N)

- Test for Orthophosphate : EPA Method 365.3 / APHA 4500-P

A brief summary is given below (Source: EPA). For details, refer to EPA Method 365.3 : Phosphorus, All Forms (Colorimetric, Ascorbic Acid, Two Reagent) or to APHA Standard Methods: 4500-P (Phosphorus)

Monitoring phosphorus involves measuring very low concentrations down to 0.01 mg/L or lower. Even such very low concentrations of phosphorus can have a dramatic impact downstream. Less sensitive methods should be used only to identify serious problem areas.

Orthophosphate is the most common form of phosphorus occurring in wastewater. It is also commonly referred to as “phosphate” and “reactive Phosphorus”. There are three colorimetric methods used to measure Total Orthophosphate to a reasonable degree of accuracy:

- Vanadomolybdo-Phosphoric Acid / ‘Yellow’ Method 
(for routine analysis in range of 1 to 20 mg/L of Ortho-P)

- Ascorbic Acid / ‘Blue’ Method (for range of 0.01 to 6 mg/L of Ortho-P)

- Stannous chloride method (for range of 0.01 to 6 mg/L of Ortho-P)

A reagent (either liquid or powder) containing ascorbic acid and ammonium molybdate reacts with orthophosphate in the sample to form either a blue or yellow compound, depending on the method. The intensity of the blue or yellow color is directly proportional to the amount of orthophosphate in the water.

- Test for Iron (Fe) : EPA 236-1 / 236-2 / APHA 3500-Fe

Total iron ion concentration is generally analyzed on-site by forming coloured compounds and measuring color intensity with spectrophotometric or visual analysis. For details, refer to EPA Method 236-1 (Direct Aspiration) or EPA Method 236-2 (Furnace) or APHA Standard Methods: 3500-Fe

- What’s a desirable range of nutrient concentration in the wastewater?

The nutrient concentrations in the influent to the Aeration Basin need to match the influent BOD strength as follows:

- Nitrogen concentration has to be at least = BOD / 20

- Phosphorus concentration has to be at least = BOD / 100

- Iron concentration has to be at least = BOD / 200

Besides monitoring for influent nutrient content, ensure the Aeration Basin effluent has 1-2 mg/L of TIN or Total Inorganic Nitrogen (ammonia plus nitrate) and Ortho-Phosphorus, each. This is a useful indicator of whether there is a nutrient deficiency in your wastewater influent. Note here, that TKN (Total Kjeldahl Nitrogen) and TP (Total Phosphorus) are not used, as they may contain organically-bound nutrients that may not be rapidly available for the bugs ("bug bodies") to keep pace with the BOD use. So they’re not a good indicator of whether or not there is nutrient deficiency.

- What should you do if there aren’t enough nutrients?
You will need to supplement nutrient levels using treatment chemicals. The next page will feature a Nutrient dosing calculator, which checks if you have enough N, P, Fe available and computes the required dosing amounts for the nutrients that are deficient. Your chemical feed equipment should be set to feed the calculated dosing amount.

- How do you ensure effective operation & maintenance of your nutrient dosing system?

- Ensure your flowmeters are cleaned and calibrated from time to time

- Ensure hand valves manually adjusted to regulate flow are not stuck. For automated flow adjustments by the VFD (Variable Frequency Drive) on your pump-motors, regularly check the settings on your HMI in the control panel. Perform manual checks using flow meters from time to time to ensure the instrumentation works accurately.

- Ensure your standby devices, pumps, etc. are in good operating condition, ready to go in case of breakdowns. Have them installed in parallel.

- Regularly clean your lines to prevent them from plugging or choking.