## Calculator
Polymer Dosing Calculator
Enter values below where required :
Step 1 : Chemical Selection
Enter the chemical you're using for Jar Testing | PAC
Enter if the chemical is in solid (dry) or liquid form | Solid (dry)
Commercial grade or Purity (% concentration) | 99%
Specific gravity of chemical (get from supplier or using a hydrometer) | 1.37
Amount of polymer in 1 gallon of your chemical | 11.3115 | lbs/gal
Step 2 : Preparing the Stock Solution
GUIDANCE :
How strong does your chemical have to be? How much do you need, so there's enough and not an excess of expensive chemical? You'll need to decide what works for your facility. Use the following for guidance.
Enter the concentration (% w/v) you desire in your stock solution (OR) (Usually, 1% for Alum, Lime, Ferric chloride, or others) (Usually, 0.01 to 0.5% for Dry or Liquid Polymers) | 1%
Select the range of polymer dosage you usually use in your facility | 50-500 mg/L
How much stock solution do you need, in mL | 500 | mL
Recommended/Desired Stock Solution Concentration (mg/L or ppm) | 10000 | mg/L or ppm
Recommended/Desired Stock Solution Concentration (%) | 1%
For Dry Materials:
Recommendation:
Dissolve 5 grams of your chemical in 500 mL of distilled water to prepare 1% stock solution.
For Liquid Materials:
Recommendation:
N/A
Step 3 : Dosing Rate
Now perform the Jar Test and decide on what's the best (optimum) chemical dosage concentration (mg/L) for your facility, or how much mL of stock solution is right for a 1 Litre wastewater sample.
Enter desired dosage concentration (mg/L), if known (OR) | 25 | mg/L or ppm
Enter desired mL of stock solution for the wastewater sample (mL) | 2.5 | mL
Enter volume of wastewater sample used in Jar test | 1000 | mL
Influent flow rate to Aeration Basin (MGD) | 0.5 | MGD
Dosing pump : Enter duration of operation (minutes) every hour | 10 | minutes per hour
OUTPUT :
Amount of polymer needed per day for dosing (lbs/day) | 104.25 | lbs/day
Volume of chemical needed per day for dosing (GPD or gal/day) | 9.2163 | GPD or gal/day
Volume of chemical needed per day for dosing (GPM or gal/min) | 0.038401 | GPM or gal/min
Volume of chemical needed per day for dosing (mL/min) | 145.3637 | mL/min