## Calculator
CALCULATION TOOL
INPUT :
Solids inventory, Aeration Basin | 45000 | lbs
Solids inventory, Secondary Clarifiers | 3000 | lbs
MLSS concentration | 2400 | mg/L
MLVSS to MLSS ratio | 0.75
RAS flow rate | 0.9 | MGD
RAS solids concentration | 8000 | mg/L
Minutes of operation of dosing pump, per hour | 30 | mins/hr
OUTPUT :
Total Solids Inventory | 48000 | lbs
5-6 lbs of Cl2 required per 1000 lbs MLVSS
Cl2 dosing amounts, required per day | 216 | lbs Cl2/day
Select your dosing chemical below :
Sodium hypochlorite (NaOCl) 5.25% | 0.44 | lbs Cl2/gal
Dosing requirement in GPD or gal/day | 490.9091 | GPD or gal/day
Dosing requirement in GPM or gal/min | 0.68182 | GPM or gal/min
Dosing requirement in mL per minute | 2580.9614 | mL ClO-/min
RAS Solids pumped/day | 60048 | lbs/day
Frequency of exposure | 2 | times/day
You need more application points to dose the RAS. Set up two or more pumps to collectively dose 2581 mL/min of Sodium hypochlorite (NaOCl) 5.25%