## Sheet1
CALCULATION TOOL - Septicity or Odor Control
Rotten odor or septicity in the form of H2S can be controlled by increasing DO through more Aeration or by dosing chemicals which act as strong oxidants like Hydrogen Peroxide (H2O2), Potassium Permanganate (KMnO4) or Chlorine. This tool computes how much H2O2 or KMnO4 you require to dose.
H2S removal
These chemicals react with H2S to reduce the sepcitiy and rotten odor, according to the equations below:
2 lb H2O2 (50% purity) for 1 lb H2S oxidised
3.5 to 5.0 lbs KMnO4 (97% purity) for 1 lb H2S oxidised
12.5 to 15.0 lbs KMnO4 (97% purity) for 1 lb H2S oxidised
INPUTS
Influent flow to Aeration Basin | 0.4 | MGD
Aqueous Hydrogen sulfide (H2S) conc in wastewater at Aeration Basin Outlet or Secondary Clarifier Center Well | 25 | mg/L or ppm
pH of wastewater at Aeration Basin Outlet or Secondary Clarifier Center Well | 8
Minutes of operation of dosing pump, per hour | 15 | mins per hour
OUTPUTS
Amount of H2S in your wastewater (lbs/d) OR | 83.4 | lbs/d
Select your dosing chemical | Potassium Permanganate (KMnO4) 97% purity
Chemical amount (lbs) required to oxidize 1 lb H2S | 13 | lbs for every lb H2S
Total dosing amount required for H2S removal (lbs/d) | 1084.2 | lbs/d
Density of dosing chemical | 22.13 | lbs/gal
Total dosing amount required for H2S removal (GPD or gal/d) | 48.9923 | GPD or gal/day
Total dosing amount required for H2S removal (GPM or gal/min) | 0.13609 | GPM or gal/min
Total dosing amount required for H2S removal (mL/min) | 515.1556 | mL/min